# SIL Verification Report

Hybrit Pilot Plant

| REV | DATE | APPROVED | DESCRIPTION OF CHANGE |
| --- | --- | --- | --- |
|  | 24 Apr 2022 |  |  |

Automatically generated by exSILentia® version 4.12.2.0.

Table of Contents

1	Purpose and Scope	32

1.1	General Project Information	32

2	SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning	33

2.1	General SIF Information	33

2.2	Safety Integrity Levels	33

2.3	SIL Verification Parameters and Results	34

2.3.1	Sensor Part Configuration	35

2.3.2	Logic Solver Part Configuration	37

2.3.3	Final Element Part Configuration	38

3	SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system	40

3.1	General SIF Information	40

3.2	Safety Integrity Levels	40

3.3	SIL Verification Parameters and Results	41

3.3.1	Sensor Part Configuration	42

3.3.2	Logic Solver Part Configuration	44

3.3.3	Final Element Part Configuration	45

4	SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100)	47

4.1	General SIF Information	47

4.2	Safety Integrity Levels	47

4.3	SIL Verification Parameters and Results	48

4.3.1	Sensor Part Configuration	49

4.3.2	Logic Solver Part Configuration	51

4.3.3	Final Element Part Configuration	52

5	SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100)	55

5.1	General SIF Information	55

5.2	Safety Integrity Levels	55

5.3	SIL Verification Parameters and Results	56

5.3.1	Sensor Part Configuration	57

5.3.2	Logic Solver Part Configuration	59

5.3.3	Final Element Part Configuration	60

6	SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101	62

6.1	General SIF Information	62

6.2	Safety Integrity Levels	62

6.3	SIL Verification Parameters and Results	63

6.3.1	Sensor Part Configuration	64

6.3.2	Logic Solver Part Configuration	66

6.3.3	Final Element Part Configuration	67

7	SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close	69

7.1	General SIF Information	69

7.2	Safety Integrity Levels	69

7.3	SIL Verification Parameters and Results	70

7.3.1	Sensor Part Configuration	71

7.3.2	Logic Solver Part Configuration	73

7.3.3	Final Element Part Configuration	74

8	SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps	76

8.1	General SIF Information	76

8.2	Safety Integrity Levels	76

8.3	SIL Verification Parameters and Results	77

8.3.1	Sensor Part Configuration	78

8.3.2	Logic Solver Part Configuration	80

8.3.3	Final Element Part Configuration	81

9	SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608	83

9.1	General SIF Information	83

9.2	Safety Integrity Levels	83

9.3	SIL Verification Parameters and Results	84

9.3.1	Sensor Part Configuration	85

9.3.2	Logic Solver Part Configuration	87

9.3.3	Final Element Part Configuration	88

10	SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100) close 347SV671 lean MEA to Absorber	90

10.1	General SIF Information	90

10.2	Safety Integrity Levels	90

10.3	SIL Verification Parameters and Results	91

10.3.1	Sensor Part Configuration	92

10.3.2	Logic Solver Part Configuration	94

10.3.3	Final Element Part Configuration	95

11	SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor (DENNA UTGÅR)	98

11.1	General SIF Information	98

11.2	Safety Integrity Levels	98

11.3	SIL Verification Parameters and Results	99

11.3.1	Sensor Part Configuration	100

11.3.2	Logic Solver Part Configuration	101

11.3.3	Final Element Part Configuration	102

12	SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2)	103

12.1	General SIF Information	103

12.2	Safety Integrity Levels	103

12.3	SIL Verification Parameters and Results	105

12.3.1	Sensor Part Configuration	106

12.3.2	Logic Solver Part Configuration	108

12.3.3	Final Element Part Configuration	109

13	SIF-011 Beräkning av SIF-011 "open"	112

13.1	General SIF Information	112

13.2	Safety Integrity Levels	112

13.3	SIL Verification Parameters and Results	114

13.3.1	Sensor Part Configuration	115

13.3.2	Logic Solver Part Configuration	115

13.3.3	Final Element Part Configuration	116

14	SIF-011 Beräkning av SIF-011 "close"	121

14.1	General SIF Information	121

14.2	Safety Integrity Levels	121

14.3	SIL Verification Parameters and Results	123

14.3.1	Sensor Part Configuration	124

14.3.2	Logic Solver Part Configuration	124

14.3.3	Final Element Part Configuration	125

15	SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2)	129

15.1	General SIF Information	129

15.2	Safety Integrity Levels	129

15.3	SIL Verification Parameters and Results	130

15.3.1	Sensor Part Configuration	131

15.3.2	Logic Solver Part Configuration	133

15.3.3	Final Element Part Configuration	134

16	SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3)	139

16.1	General SIF Information	139

16.2	Safety Integrity Levels	139

16.3	SIL Verification Parameters and Results	140

16.3.1	Sensor Part Configuration	141

16.3.2	Logic Solver Part Configuration	143

16.3.3	Final Element Part Configuration	144

17	SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2)	146

17.1	General SIF Information	146

17.2	Safety Integrity Levels	146

17.3	SIL Verification Parameters and Results	148

17.3.1	Sensor Part Configuration	149

17.3.2	Logic Solver Part Configuration	151

17.3.3	Final Element Part Configuration	152

18	SIF-016 SIL1 Temp överhettad ånga (271TI552|L2)	157

18.1	General SIF Information	157

18.2	Safety Integrity Levels	157

18.3	SIL Verification Parameters and Results	158

18.3.1	Sensor Part Configuration	159

18.3.2	Logic Solver Part Configuration	161

18.3.3	Final Element Part Configuration	162

19	SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)	164

19.1	General SIF Information	164

19.2	Safety Integrity Levels	164

19.3	SIL Verification Parameters and Results	165

19.3.1	Sensor Part Configuration	166

19.3.2	Logic Solver Part Configuration	168

19.3.3	Final Element Part Configuration	169

20	SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)	171

20.1	General SIF Information	171

20.2	Safety Integrity Levels	171

20.3	SIL Verification Parameters and Results	172

20.3.1	Sensor Part Configuration	173

20.3.2	Logic Solver Part Configuration	176

20.3.3	Final Element Part Configuration	177

21	SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2)	180

21.1	General SIF Information	180

21.2	Safety Integrity Levels	180

21.3	SIL Verification Parameters and Results	182

21.3.1	Sensor Part Configuration	183

21.3.2	Logic Solver Part Configuration	188

21.3.3	Final Element Part Configuration	189

22	SIF-020 SIL2 Difftryck O2-transferline (251XI313)	193

22.1	General SIF Information	193

22.2	Safety Integrity Levels	193

22.3	SIL Verification Parameters and Results	194

22.3.1	Sensor Part Configuration	195

22.3.2	Logic Solver Part Configuration	198

22.3.3	Final Element Part Configuration	199

23	SIF-021 SIL1 Gastryck transferline (344PZ321|L2)	201

23.1	General SIF Information	201

23.2	Safety Integrity Levels	201

23.3	SIL Verification Parameters and Results	202

23.3.1	Sensor Part Configuration	203

23.3.2	Logic Solver Part Configuration	205

23.3.3	Final Element Part Configuration	206

24	SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2)	208

24.1	General SIF Information	208

24.2	Safety Integrity Levels	208

24.3	SIL Verification Parameters and Results	209

24.3.1	Sensor Part Configuration	210

24.3.2	Logic Solver Part Configuration	212

24.3.3	Final Element Part Configuration	213

25	SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2)	215

25.1	General SIF Information	215

25.2	Safety Integrity Levels	215

25.3	SIL Verification Parameters and Results	216

25.3.1	Sensor Part Configuration	217

25.3.2	Logic Solver Part Configuration	221

25.3.3	Final Element Part Configuration	222

26	SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)	225

26.1	General SIF Information	225

26.2	Safety Integrity Levels	225

26.3	SIL Verification Parameters and Results	227

26.3.1	Sensor Part Configuration	228

26.3.2	Logic Solver Part Configuration	231

26.3.3	Final Element Part Configuration	232

27	SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2)	235

27.1	General SIF Information	235

27.2	Safety Integrity Levels	235

27.3	SIL Verification Parameters and Results	237

27.3.1	Sensor Part Configuration	238

27.3.2	Logic Solver Part Configuration	240

27.3.3	Final Element Part Configuration	241

28	SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2)	246

28.1	General SIF Information	246

28.2	Safety Integrity Levels	246

28.3	SIL Verification Parameters and Results	247

28.3.1	Sensor Part Configuration	248

28.3.2	Logic Solver Part Configuration	252

28.3.3	Final Element Part Configuration	253

29	SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2)	255

29.1	General SIF Information	255

29.2	Safety Integrity Levels	255

29.3	SIL Verification Parameters and Results	257

29.3.1	Sensor Part Configuration	258

29.3.2	Logic Solver Part Configuration	260

29.3.3	Final Element Part Configuration	261

30	SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2)	265

30.1	General SIF Information	265

30.2	Safety Integrity Levels	265

30.3	SIL Verification Parameters and Results	266

30.3.1	Sensor Part Configuration	267

30.3.2	Logic Solver Part Configuration	269

30.3.3	Final Element Part Configuration	270

31	SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2)	272

31.1	General SIF Information	272

31.2	Safety Integrity Levels	272

31.3	SIL Verification Parameters and Results	274

31.3.1	Sensor Part Configuration	275

31.3.2	Logic Solver Part Configuration	277

31.3.3	Final Element Part Configuration	278

32	SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2)	282

32.1	General SIF Information	282

32.2	Safety Integrity Levels	282

32.3	SIL Verification Parameters and Results	284

32.3.1	Sensor Part Configuration	285

32.3.2	Logic Solver Part Configuration	287

32.3.3	Final Element Part Configuration	288

33	SIF-032 SIL2 Flamvakt (344YS314|SG1)	292

33.1	General SIF Information	292

33.2	Safety Integrity Levels	292

33.3	SIL Verification Parameters and Results	294

33.3.1	Sensor Part Configuration	295

33.3.2	Logic Solver Part Configuration	297

33.3.3	Final Element Part Configuration	298

34	SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2)	301

34.1	General SIF Information	301

34.2	Safety Integrity Levels	301

34.3	SIL Verification Parameters and Results	302

34.3.1	Sensor Part Configuration	303

34.3.2	Logic Solver Part Configuration	305

34.3.3	Final Element Part Configuration	306

35	SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2)	308

35.1	General SIF Information	308

35.2	Safety Integrity Levels	308

35.3	SIL Verification Parameters and Results	309

35.3.1	Sensor Part Configuration	310

35.3.2	Logic Solver Part Configuration	312

35.3.3	Final Element Part Configuration	313

36	SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2)	315

36.1	General SIF Information	315

36.2	Safety Integrity Levels	315

36.3	SIL Verification Parameters and Results	316

36.3.1	Sensor Part Configuration	318

36.3.2	Logic Solver Part Configuration	324

36.3.3	Final Element Part Configuration	325

37	SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2)	328

37.1	General SIF Information	328

37.2	Safety Integrity Levels	328

37.3	SIL Verification Parameters and Results	329

37.3.1	Sensor Part Configuration	330

37.3.2	Logic Solver Part Configuration	332

37.3.3	Final Element Part Configuration	333

38	SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2)	337

38.1	General SIF Information	337

38.2	Safety Integrity Levels	337

38.3	SIL Verification Parameters and Results	338

38.3.1	Sensor Part Configuration	340

38.3.2	Logic Solver Part Configuration	341

38.3.3	Final Element Part Configuration	342

39	SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2)	351

39.1	General SIF Information	351

39.2	Safety Integrity Levels	351

39.3	SIL Verification Parameters and Results	352

39.3.1	Sensor Part Configuration	353

39.3.2	Logic Solver Part Configuration	355

39.3.3	Final Element Part Configuration	356

40	SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2)	359

40.1	General SIF Information	359

40.2	Safety Integrity Levels	359

40.3	SIL Verification Parameters and Results	360

40.3.1	Sensor Part Configuration	361

40.3.2	Logic Solver Part Configuration	363

40.3.3	Final Element Part Configuration	364

41	SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2)	369

41.1	General SIF Information	369

41.2	Safety Integrity Levels	369

41.3	SIL Verification Parameters and Results	370

41.3.1	Sensor Part Configuration	371

41.3.2	Logic Solver Part Configuration	373

41.3.3	Final Element Part Configuration	374

42	SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2)	379

42.1	General SIF Information	379

42.2	Safety Integrity Levels	379

42.3	SIL Verification Parameters and Results	380

42.3.1	Sensor Part Configuration	381

42.3.2	Logic Solver Part Configuration	383

42.3.3	Final Element Part Configuration	384

43	SIF-042 SIL1 Temp kondensor processgas (353TI301|H2)	389

43.1	General SIF Information	389

43.2	Safety Integrity Levels	389

43.3	SIL Verification Parameters and Results	390

43.3.1	Sensor Part Configuration	391

43.3.2	Logic Solver Part Configuration	393

43.3.3	Final Element Part Configuration	394

44	SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2)	397

44.1	General SIF Information	397

44.2	Safety Integrity Levels	397

44.3	SIL Verification Parameters and Results	398

44.3.1	Sensor Part Configuration	399

44.3.2	Logic Solver Part Configuration	401

44.3.3	Final Element Part Configuration	402

45	SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2)	409

45.1	General SIF Information	409

45.2	Safety Integrity Levels	409

45.3	SIL Verification Parameters and Results	410

45.3.1	Sensor Part Configuration	411

45.3.2	Logic Solver Part Configuration	413

45.3.3	Final Element Part Configuration	414

46	SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2)	421

46.1	General SIF Information	421

46.2	Safety Integrity Levels	421

46.3	SIL Verification Parameters and Results	422

46.3.1	Sensor Part Configuration	423

46.3.2	Logic Solver Part Configuration	425

46.3.3	Final Element Part Configuration	426

47	SIF-046 SIL2 Skintemp quench processgas (353TI308|H2)	432

47.1	General SIF Information	432

47.2	Safety Integrity Levels	432

47.3	SIL Verification Parameters and Results	433

47.3.1	Sensor Part Configuration	434

47.3.2	Logic Solver Part Configuration	436

47.3.3	Final Element Part Configuration	437

48	SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2)	441

48.1	General SIF Information	441

48.2	Safety Integrity Levels	441

48.3	SIL Verification Parameters and Results	442

48.3.1	Sensor Part Configuration	443

48.3.2	Logic Solver Part Configuration	445

48.3.3	Final Element Part Configuration	446

49	SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2)	451

49.1	General SIF Information	451

49.2	Safety Integrity Levels	451

49.3	SIL Verification Parameters and Results	452

49.3.1	Sensor Part Configuration	453

49.3.2	Logic Solver Part Configuration	455

49.3.3	Final Element Part Configuration	456

50	SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2)	460

50.1	General SIF Information	460

50.2	Safety Integrity Levels	460

50.3	SIL Verification Parameters and Results	461

50.3.1	Sensor Part Configuration	462

50.3.2	Logic Solver Part Configuration	464

50.3.3	Final Element Part Configuration	465

51	SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2)	467

51.1	General SIF Information	467

51.2	Safety Integrity Levels	467

51.3	SIL Verification Parameters and Results	468

51.3.1	Sensor Part Configuration	469

51.3.2	Logic Solver Part Configuration	471

51.3.3	Final Element Part Configuration	472

52	SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2)	474

52.1	General SIF Information	474

52.2	Safety Integrity Levels	474

52.3	SIL Verification Parameters and Results	475

52.3.1	Sensor Part Configuration	476

52.3.2	Logic Solver Part Configuration	478

52.3.3	Final Element Part Configuration	479

53	SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2)	481

53.1	General SIF Information	481

53.2	Safety Integrity Levels	481

53.3	SIL Verification Parameters and Results	482

53.3.1	Sensor Part Configuration	483

53.3.2	Logic Solver Part Configuration	485

53.3.3	Final Element Part Configuration	486

54	SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2)	488

54.1	General SIF Information	488

54.2	Safety Integrity Levels	488

54.3	SIL Verification Parameters and Results	489

54.3.1	Sensor Part Configuration	490

54.3.2	Logic Solver Part Configuration	492

54.3.3	Final Element Part Configuration	493

55	SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	495

55.1	General SIF Information	495

55.2	Safety Integrity Levels	495

55.3	SIL Verification Parameters and Results	496

55.3.1	Sensor Part Configuration	497

55.3.2	Logic Solver Part Configuration	499

55.3.3	Final Element Part Configuration	500

56	SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2)	502

56.1	General SIF Information	502

56.2	Safety Integrity Levels	502

56.3	SIL Verification Parameters and Results	503

56.3.1	Sensor Part Configuration	504

56.3.2	Logic Solver Part Configuration	506

56.3.3	Final Element Part Configuration	507

57	SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	509

57.1	General SIF Information	509

57.2	Safety Integrity Levels	509

57.3	SIL Verification Parameters and Results	510

57.3.1	Sensor Part Configuration	511

57.3.2	Logic Solver Part Configuration	513

57.3.3	Final Element Part Configuration	514

58	SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2)	516

58.1	General SIF Information	516

58.2	Safety Integrity Levels	516

58.3	SIL Verification Parameters and Results	517

58.3.1	Sensor Part Configuration	518

58.3.2	Logic Solver Part Configuration	520

58.3.3	Final Element Part Configuration	521

59	SIF-058 SIL1 Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015)	523

59.1	General SIF Information	523

59.2	Safety Integrity Levels	523

59.3	SIL Verification Parameters and Results	524

59.3.1	Sensor Part Configuration	525

59.3.2	Logic Solver Part Configuration	527

59.3.3	Final Element Part Configuration	528

60	SIF-059 SIL2 Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566)	530

60.1	General SIF Information	530

60.2	Safety Integrity Levels	530

60.3	SIL Verification Parameters and Results	531

60.3.1	Sensor Part Configuration	532

60.3.2	Logic Solver Part Configuration	535

60.3.3	Final Element Part Configuration	536

61	SIF-060 SIL2 Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634)	540

61.1	General SIF Information	540

61.2	Safety Integrity Levels	540

61.3	SIL Verification Parameters and Results	541

61.3.1	Sensor Part Configuration	542

61.3.2	Logic Solver Part Configuration	544

61.3.3	Final Element Part Configuration	545

62	SIF-061 SIL2 Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 )	547

62.1	General SIF Information	547

62.2	Safety Integrity Levels	547

62.3	SIL Verification Parameters and Results	548

62.3.1	Sensor Part Configuration	549

62.3.2	Logic Solver Part Configuration	551

62.3.3	Final Element Part Configuration	552

63	SIF-062 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634)	556

63.1	General SIF Information	556

63.2	Safety Integrity Levels	556

63.3	SIL Verification Parameters and Results	557

63.3.1	Sensor Part Configuration	558

63.3.2	Logic Solver Part Configuration	560

63.3.3	Final Element Part Configuration	561

64	SIF-063 SIL2 Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522)	563

64.1	General SIF Information	563

64.2	Safety Integrity Levels	563

64.3	SIL Verification Parameters and Results	564

64.3.1	Sensor Part Configuration	565

64.3.2	Logic Solver Part Configuration	567

64.3.3	Final Element Part Configuration	568

65	SIF-064 SIL2 Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521)	570

65.1	General SIF Information	570

65.2	Safety Integrity Levels	570

65.3	SIL Verification Parameters and Results	571

65.3.1	Sensor Part Configuration	572

65.3.2	Logic Solver Part Configuration	574

65.3.3	Final Element Part Configuration	575

66	SIF-065 SIL2 Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520)	577

66.1	General SIF Information	577

66.2	Safety Integrity Levels	577

66.3	SIL Verification Parameters and Results	578

66.3.1	Sensor Part Configuration	579

66.3.2	Logic Solver Part Configuration	581

66.3.3	Final Element Part Configuration	582

67	SIF-066 SIL2 Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) => Close Avstängning tillopp spolvatten (345SV634)	584

67.1	General SIF Information	584

67.2	Safety Integrity Levels	584

67.3	SIL Verification Parameters and Results	585

67.3.1	Sensor Part Configuration	586

67.3.2	Logic Solver Part Configuration	589

67.3.3	Final Element Part Configuration	590

68	SIF-067 SIL1 Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015)	593

68.1	General SIF Information	593

68.2	Safety Integrity Levels	593

68.3	SIL Verification Parameters and Results	594

68.3.1	Sensor Part Configuration	595

68.3.2	Logic Solver Part Configuration	597

68.3.3	Final Element Part Configuration	598

69	SIF-068 SIL2 Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 )	600

69.1	General SIF Information	600

69.2	Safety Integrity Levels	600

69.3	SIL Verification Parameters and Results	601

69.3.1	Sensor Part Configuration	602

69.3.2	Logic Solver Part Configuration	605

69.3.3	Final Element Part Configuration	606

70	SIF-069 SIL2 Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635)	609

70.1	General SIF Information	609

70.2	Safety Integrity Levels	609

70.3	SIL Verification Parameters and Results	610

70.3.1	Sensor Part Configuration	611

70.3.2	Logic Solver Part Configuration	613

70.3.3	Final Element Part Configuration	614

71	SIF-070 SIL2 Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 )	616

71.1	General SIF Information	616

71.2	Safety Integrity Levels	616

71.3	SIL Verification Parameters and Results	617

71.3.1	Sensor Part Configuration	618

71.3.2	Logic Solver Part Configuration	620

71.3.3	Final Element Part Configuration	621

72	SIF-071 SIL2 Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635)	623

72.1	General SIF Information	623

72.2	Safety Integrity Levels	623

72.3	SIL Verification Parameters and Results	624

72.3.1	Sensor Part Configuration	625

72.3.2	Logic Solver Part Configuration	627

72.3.3	Final Element Part Configuration	628

73	SIF-072 SIL2 Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522)	630

73.1	General SIF Information	630

73.2	Safety Integrity Levels	630

73.3	SIL Verification Parameters and Results	631

73.3.1	Sensor Part Configuration	632

73.3.2	Logic Solver Part Configuration	634

73.3.3	Final Element Part Configuration	635

74	SIF-073 SIL2 Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521)	637

74.1	General SIF Information	637

74.2	Safety Integrity Levels	637

74.3	SIL Verification Parameters and Results	638

74.3.1	Sensor Part Configuration	639

74.3.2	Logic Solver Part Configuration	641

74.3.3	Final Element Part Configuration	642

75	SIF-074 SIL2 Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520)	644

75.1	General SIF Information	644

75.2	Safety Integrity Levels	644

75.3	SIL Verification Parameters and Results	645

75.3.1	Sensor Part Configuration	646

75.3.2	Logic Solver Part Configuration	648

75.3.3	Final Element Part Configuration	649

76	SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582)	651

76.1	General SIF Information	651

76.2	Safety Integrity Levels	651

76.3	SIL Verification Parameters and Results	652

76.3.1	Sensor Part Configuration	653

76.3.2	Logic Solver Part Configuration	656

76.3.3	Final Element Part Configuration	657

77	SIF-076 SIL2 Hög nivå i ångpanna 271AG001 (271LZ316|H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556)	660

77.1	General SIF Information	660

77.2	Safety Integrity Levels	660

77.3	SIL Verification Parameters and Results	661

77.3.1	Sensor Part Configuration	662

77.3.2	Logic Solver Part Configuration	664

77.3.3	Final Element Part Configuration	665

78	SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) => Close Avstängningsventil O2 efter tankpark (251SV520)	667

78.1	General SIF Information	667

78.2	Safety Integrity Levels	667

78.3	SIL Verification Parameters and Results	668

78.3.1	Sensor Part Configuration	669

78.3.2	Logic Solver Part Configuration	671

78.3.3	Final Element Part Configuration	672

79	SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631	674

79.1	General SIF Information	674

79.2	Safety Integrity Levels	674

79.3	SIL Verification Parameters and Results	675

79.3.1	Sensor Part Configuration	676

79.3.2	Logic Solver Part Configuration	677

79.3.3	Final Element Part Configuration	678

80	SIF-079 SIL2 341PZ401 (H2/L2) => close H2	680

80.1	General SIF Information	680

80.2	Safety Integrity Levels	680

80.3	SIL Verification Parameters and Results	681

80.3.1	Sensor Part Configuration	682

80.3.2	Logic Solver Part Configuration	684

80.3.3	Final Element Part Configuration	685

81	SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556	692

81.1	General SIF Information	692

81.2	Safety Integrity Levels	692

81.3	SIL Verification Parameters and Results	693

81.3.1	Sensor Part Configuration	694

81.3.2	Logic Solver Part Configuration	696

81.3.3	Final Element Part Configuration	697

82	SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K	700

82.1	General SIF Information	700

82.2	Safety Integrity Levels	700

82.3	SIL Verification Parameters and Results	701

82.3.1	Sensor Part Configuration	702

82.3.2	Logic Solver Part Configuration	705

82.3.3	Final Element Part Configuration	706

83	SIF-082 SIL2 252PZ337 (H2/L2) => close NG	709

83.1	General SIF Information	709

83.2	Safety Integrity Levels	709

83.3	SIL Verification Parameters and Results	710

83.3.1	Sensor Part Configuration	711

83.3.2	Logic Solver Part Configuration	713

83.3.3	Final Element Part Configuration	714

84	SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)	716

84.1	General SIF Information	716

84.2	Safety Integrity Levels	716

84.3	SIL Verification Parameters and Results	717

84.3.1	Sensor Part Configuration	718

84.3.2	Logic Solver Part Configuration	721

84.3.3	Final Element Part Configuration	722

85	SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2)	725

85.1	General SIF Information	725

85.2	Safety Integrity Levels	725

85.3	SIL Verification Parameters and Results	726

85.3.1	Sensor Part Configuration	727

85.3.2	Logic Solver Part Configuration	729

85.3.3	Final Element Part Configuration	730

86	SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift (344MA001_RUN_N)	733

86.1	General SIF Information	733

86.2	Safety Integrity Levels	733

86.3	SIL Verification Parameters and Results	734

86.3.1	Sensor Part Configuration	735

86.3.2	Logic Solver Part Configuration	738

86.3.3	Final Element Part Configuration	739

87	SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH) => Stop electrolyzer A	743

87.1	General SIF Information	743

87.2	Safety Integrity Levels	743

87.3	SIL Verification Parameters and Results	744

87.3.1	Sensor Part Configuration	745

87.3.2	Logic Solver Part Configuration	747

87.3.3	Final Element Part Configuration	748

88	SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH) => Stop electrolyzer A	750

88.1	General SIF Information	750

88.2	Safety Integrity Levels	750

88.3	SIL Verification Parameters and Results	751

88.3.1	Sensor Part Configuration	752

88.3.2	Logic Solver Part Configuration	754

88.3.3	Final Element Part Configuration	755

89	SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH) => Stop electrolyzer B	757

89.1	General SIF Information	757

89.2	Safety Integrity Levels	757

89.3	SIL Verification Parameters and Results	758

89.3.1	Sensor Part Configuration	759

89.3.2	Logic Solver Part Configuration	761

89.3.3	Final Element Part Configuration	762

90	SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH) => Stop electrolyzer B	764

90.1	General SIF Information	764

90.2	Safety Integrity Levels	764

90.3	SIL Verification Parameters and Results	765

90.3.1	Sensor Part Configuration	766

90.3.2	Logic Solver Part Configuration	768

90.3.3	Final Element Part Configuration	769

91	SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL) => Stop electrolyzer A	771

91.1	General SIF Information	771

91.2	Safety Integrity Levels	771

91.3	SIL Verification Parameters and Results	772

91.3.1	Sensor Part Configuration	773

91.3.2	Logic Solver Part Configuration	775

91.3.3	Final Element Part Configuration	776

92	SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL) => Stop electrolyzer B	778

92.1	General SIF Information	778

92.2	Safety Integrity Levels	778

92.3	SIL Verification Parameters and Results	779

92.3.1	Sensor Part Configuration	780

92.3.2	Logic Solver Part Configuration	782

92.3.3	Final Element Part Configuration	783

93	SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer A and successfull nitrogen purging	785

93.1	General SIF Information	785

93.2	Safety Integrity Levels	785

93.3	SIL Verification Parameters and Results	786

93.3.1	Sensor Part Configuration	787

93.3.2	Logic Solver Part Configuration	789

93.3.3	Final Element Part Configuration	790

94	SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH) => Stop electrolyzer B and successfull nitrogen purging	795

94.1	General SIF Information	795

94.2	Safety Integrity Levels	795

94.3	SIL Verification Parameters and Results	796

94.3.1	Sensor Part Configuration	797

94.3.2	Logic Solver Part Configuration	799

94.3.3	Final Element Part Configuration	800

95	SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL) => Stop electrolyzer A	805

95.1	General SIF Information	805

95.2	Safety Integrity Levels	805

95.3	SIL Verification Parameters and Results	806

95.3.1	Sensor Part Configuration	807

95.3.2	Logic Solver Part Configuration	809

95.3.3	Final Element Part Configuration	810

96	SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL) => Stop electrolyzer B	812

96.1	General SIF Information	812

96.2	Safety Integrity Levels	812

96.3	SIL Verification Parameters and Results	813

96.3.1	Sensor Part Configuration	814

96.3.2	Logic Solver Part Configuration	816

96.3.3	Final Element Part Configuration	817

97	SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133	819

97.1	General SIF Information	819

97.2	Safety Integrity Levels	819

97.3	SIL Verification Parameters and Results	820

97.3.1	Sensor Part Configuration	822

97.3.2	Logic Solver Part Configuration	823

97.3.3	Final Element Part Configuration	824

98	SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133	830

98.1	General SIF Information	830

98.2	Safety Integrity Levels	830

98.3	SIL Verification Parameters and Results	831

98.3.1	Sensor Part Configuration	833

98.3.2	Logic Solver Part Configuration	834

98.3.3	Final Element Part Configuration	835

99	SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H) => Stop Comp. A motor 341PU132	841

99.1	General SIF Information	841

99.2	Safety Integrity Levels	841

99.3	SIL Verification Parameters and Results	842

99.3.1	Sensor Part Configuration	843

99.3.2	Logic Solver Part Configuration	845

99.3.3	Final Element Part Configuration	846

100	SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132	848

100.1	General SIF Information	848

100.2	Safety Integrity Levels	848

100.3	SIL Verification Parameters and Results	849

100.3.1	Sensor Part Configuration	850

100.3.2	Logic Solver Part Configuration	852

100.3.3	Final Element Part Configuration	853

101	SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL ) => Close 341SV926	855

101.1	General SIF Information	855

101.2	Safety Integrity Levels	855

101.3	SIL Verification Parameters and Results	856

101.3.1	Sensor Part Configuration	857

101.3.2	Logic Solver Part Configuration	859

101.3.3	Final Element Part Configuration	860

102	SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH) => Stop Comp. A motor 341PU132	862

102.1	General SIF Information	862

102.2	Safety Integrity Levels	862

102.3	SIL Verification Parameters and Results	863

102.3.1	Sensor Part Configuration	864

102.3.2	Logic Solver Part Configuration	866

102.3.3	Final Element Part Configuration	867

103	SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132	869

103.1	General SIF Information	869

103.2	Safety Integrity Levels	869

103.3	SIL Verification Parameters and Results	870

103.3.1	Sensor Part Configuration	871

103.3.2	Logic Solver Part Configuration	873

103.3.3	Final Element Part Configuration	874

104	SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133	876

104.1	General SIF Information	876

104.2	Safety Integrity Levels	876

104.3	SIL Verification Parameters and Results	877

104.3.1	Sensor Part Configuration	878

104.3.2	Logic Solver Part Configuration	880

104.3.3	Final Element Part Configuration	881

105	SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133	883

105.1	General SIF Information	883

105.2	Safety Integrity Levels	883

105.3	SIL Verification Parameters and Results	884

105.3.1	Sensor Part Configuration	885

105.3.2	Logic Solver Part Configuration	887

105.3.3	Final Element Part Configuration	888

106	SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966	890

106.1	General SIF Information	890

106.2	Safety Integrity Levels	890

106.3	SIL Verification Parameters and Results	891

106.3.1	Sensor Part Configuration	892

106.3.2	Logic Solver Part Configuration	894

106.3.3	Final Element Part Configuration	895

107	SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH) => Stop Comp. B motor 341PU133	897

107.1	General SIF Information	897

107.2	Safety Integrity Levels	897

107.3	SIL Verification Parameters and Results	898

107.3.1	Sensor Part Configuration	899

107.3.2	Logic Solver Part Configuration	901

107.3.3	Final Element Part Configuration	902

108	SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133	904

108.1	General SIF Information	904

108.2	Safety Integrity Levels	904

108.3	SIL Verification Parameters and Results	905

108.3.1	Sensor Part Configuration	906

108.3.2	Logic Solver Part Configuration	908

108.3.3	Final Element Part Configuration	909

109	SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999	911

109.1	General SIF Information	911

109.2	Safety Integrity Levels	911

109.3	SIL Verification Parameters and Results	912

109.3.1	Sensor Part Configuration	913

109.3.2	Logic Solver Part Configuration	915

109.3.3	Final Element Part Configuration	916

110	SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H) => Stop Comp. A motor 341PU132	918

110.1	General SIF Information	918

110.2	Safety Integrity Levels	918

110.3	SIL Verification Parameters and Results	919

110.3.1	Sensor Part Configuration	920

110.3.2	Logic Solver Part Configuration	922

110.3.3	Final Element Part Configuration	923

111	SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133	925

111.1	General SIF Information	925

111.2	Safety Integrity Levels	925

111.3	SIL Verification Parameters and Results	926

111.3.1	Sensor Part Configuration	927

111.3.2	Logic Solver Part Configuration	929

111.3.3	Final Element Part Configuration	930

112	SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence) => Stop electrolyzer A+B (prevent start) SIL2 | Pressure after dryer (341PZ371 L2) => Stop electrolyzer A+B (prevent start)	932

112.1	General SIF Information	932

112.2	Safety Integrity Levels	932

112.3	SIL Verification Parameters and Results	934

112.3.1	Sensor Part Configuration	935

112.3.2	Logic Solver Part Configuration	937

112.3.3	Final Element Part Configuration	938

113	SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240	942

113.1	General SIF Information	942

113.2	Safety Integrity Levels	942

113.3	SIL Verification Parameters and Results	943

113.3.1	Sensor Part Configuration	944

113.3.2	Logic Solver Part Configuration	946

113.3.3	Final Element Part Configuration	947

114	SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240	949

114.1	General SIF Information	949

114.2	Safety Integrity Levels	949

114.3	SIL Verification Parameters and Results	950

114.3.1	Sensor Part Configuration	951

114.3.2	Logic Solver Part Configuration	953

114.3.3	Final Element Part Configuration	954

115	SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240	956

115.1	General SIF Information	956

115.2	Safety Integrity Levels	956

115.3	SIL Verification Parameters and Results	957

115.3.1	Sensor Part Configuration	958

115.3.2	Logic Solver Part Configuration	960

115.3.3	Final Element Part Configuration	961

116	SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2)	963

116.1	General SIF Information	963

116.2	Safety Integrity Levels	963

116.3	SIL Verification Parameters and Results	964

116.3.1	Sensor Part Configuration	965

116.3.2	Logic Solver Part Configuration	967

116.3.3	Final Element Part Configuration	968

117	SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230	974

117.1	General SIF Information	974

117.2	Safety Integrity Levels	974

117.3	SIL Verification Parameters and Results	975

117.3.1	Sensor Part Configuration	976

117.3.2	Logic Solver Part Configuration	978

117.3.3	Final Element Part Configuration	979

118	SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230	981

118.1	General SIF Information	981

118.2	Safety Integrity Levels	981

118.3	SIL Verification Parameters and Results	982

118.3.1	Sensor Part Configuration	983

118.3.2	Logic Solver Part Configuration	985

118.3.3	Final Element Part Configuration	986

119	SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230	988

119.1	General SIF Information	988

119.2	Safety Integrity Levels	988

119.3	SIL Verification Parameters and Results	989

119.3.1	Sensor Part Configuration	990

119.3.2	Logic Solver Part Configuration	992

119.3.3	Final Element Part Configuration	993

120	SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2)	995

120.1	General SIF Information	995

120.2	Safety Integrity Levels	995

120.3	SIL Verification Parameters and Results	996

120.3.1	Sensor Part Configuration	997

120.3.2	Logic Solver Part Configuration	999

120.3.3	Final Element Part Configuration	1000

121	SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2)	1004

121.1	General SIF Information	1004

121.2	Safety Integrity Levels	1004

121.3	SIL Verification Parameters and Results	1005

121.3.1	Sensor Part Configuration	1006

121.3.2	Logic Solver Part Configuration	1008

121.3.3	Final Element Part Configuration	1009

122	SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3)	1013

122.1	General SIF Information	1013

122.2	Safety Integrity Levels	1013

122.3	SIL Verification Parameters and Results	1014

122.3.1	Sensor Part Configuration	1015

122.3.2	Logic Solver Part Configuration	1017

122.3.3	Final Element Part Configuration	1018

123	SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging	1020

123.1	General SIF Information	1020

123.2	Safety Integrity Levels	1020

123.3	SIL Verification Parameters and Results	1021

123.3.1	Sensor Part Configuration	1022

123.3.2	Logic Solver Part Configuration	1024

123.3.3	Final Element Part Configuration	1025

124	SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging	1030

124.1	General SIF Information	1030

124.2	Safety Integrity Levels	1030

124.3	SIL Verification Parameters and Results	1031

124.3.1	Sensor Part Configuration	1032

124.3.2	Logic Solver Part Configuration	1034

124.3.3	Final Element Part Configuration	1035

125	SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH) => Stop heater 341HE266	1040

125.1	General SIF Information	1040

125.2	Safety Integrity Levels	1040

125.3	SIL Verification Parameters and Results	1041

125.3.1	Sensor Part Configuration	1042

125.3.2	Logic Solver Part Configuration	1044

125.3.3	Final Element Part Configuration	1045

126	SIF-127 SIL2 Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar)	1047

126.1	General SIF Information	1047

126.2	Safety Integrity Levels	1047

126.3	SIL Verification Parameters and Results	1048

126.3.1	Sensor Part Configuration	1049

126.3.2	Logic Solver Part Configuration	1052

126.3.3	Final Element Part Configuration	1053

127	SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326)	1055

127.1	General SIF Information	1055

127.2	Safety Integrity Levels	1055

127.3	SIL Verification Parameters and Results	1056

127.3.1	Sensor Part Configuration	1057

127.3.2	Logic Solver Part Configuration	1059

127.3.3	Final Element Part Configuration	1060

128	SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326)	1063

128.1	General SIF Information	1063

128.2	Safety Integrity Levels	1063

128.3	SIL Verification Parameters and Results	1064

128.3.1	Sensor Part Configuration	1065

128.3.2	Logic Solver Part Configuration	1068

128.3.3	Final Element Part Configuration	1069

129	SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5))	1071

129.1	General SIF Information	1071

129.2	Safety Integrity Levels	1071

129.3	SIL Verification Parameters and Results	1072

129.3.1	Sensor Part Configuration	1073

129.3.2	Logic Solver Part Configuration	1076

129.3.3	Final Element Part Configuration	1077

130	SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5))	1079

130.1	General SIF Information	1079

130.2	Safety Integrity Levels	1079

130.3	SIL Verification Parameters and Results	1080

130.3.1	Sensor Part Configuration	1081

130.3.2	Logic Solver Part Configuration	1084

130.3.3	Final Element Part Configuration	1085

131	SIF-132 SIL3 | High pressure downstream of 356RV558 => close 356SV563 & 356SV564 (1oo2)	1088

131.1	General SIF Information	1088

131.2	Safety Integrity Levels	1088

131.3	SIL Verification Parameters and Results	1089

131.3.1	Sensor Part Configuration	1090

131.3.2	Logic Solver Part Configuration	1092

131.3.3	Final Element Part Configuration	1093

132	SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100)	1095

132.1	General SIF Information	1095

132.2	Safety Integrity Levels	1095

132.3	SIL Verification Parameters and Results	1096

132.3.1	Sensor Part Configuration	1097

132.3.2	Logic Solver Part Configuration	1099

132.3.3	Final Element Part Configuration	1100

133	SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	1103

133.1	General SIF Information	1103

133.2	Safety Integrity Levels	1103

133.3	SIL Verification Parameters and Results	1104

133.3.1	Sensor Part Configuration	1105

133.3.2	Logic Solver Part Configuration	1107

133.3.3	Final Element Part Configuration	1108

134	SIF-135 SIL1 High level (347LS305) filter separator 347SE101	1110

134.1	General SIF Information	1110

134.2	Safety Integrity Levels	1110

134.3	SIL Verification Parameters and Results	1111

134.3.1	Sensor Part Configuration	1112

134.3.2	Logic Solver Part Configuration	1114

134.3.3	Final Element Part Configuration	1115

135	SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002	1117

135.1	General SIF Information	1117

135.2	Safety Integrity Levels	1117

135.3	SIL Verification Parameters and Results	1118

135.3.1	Sensor Part Configuration	1119

135.3.2	Logic Solver Part Configuration	1121

135.3.3	Final Element Part Configuration	1122

136	SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002	1124

136.1	General SIF Information	1124

136.2	Safety Integrity Levels	1124

136.3	SIL Verification Parameters and Results	1125

136.3.1	Sensor Part Configuration	1126

136.3.2	Logic Solver Part Configuration	1128

136.3.3	Final Element Part Configuration	1129

137	SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002	1131

137.1	General SIF Information	1131

137.2	Safety Integrity Levels	1131

137.3	SIL Verification Parameters and Results	1132

137.3.1	Sensor Part Configuration	1133

137.3.2	Logic Solver Part Configuration	1135

137.3.3	Final Element Part Configuration	1136

138	SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002	1138

138.1	General SIF Information	1138

138.2	Safety Integrity Levels	1138

138.3	SIL Verification Parameters and Results	1139

138.3.1	Sensor Part Configuration	1140

138.3.2	Logic Solver Part Configuration	1142

138.3.3	Final Element Part Configuration	1143

139	SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002	1145

139.1	General SIF Information	1145

139.2	Safety Integrity Levels	1145

139.3	SIL Verification Parameters and Results	1146

139.3.1	Sensor Part Configuration	1147

139.3.2	Logic Solver Part Configuration	1149

139.3.3	Final Element Part Configuration	1150

140	SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002	1152

140.1	General SIF Information	1152

140.2	Safety Integrity Levels	1152

140.3	SIL Verification Parameters and Results	1153

140.3.1	Sensor Part Configuration	1154

140.3.2	Logic Solver Part Configuration	1156

140.3.3	Final Element Part Configuration	1157

141	SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater	1159

141.1	General SIF Information	1159

141.2	Safety Integrity Levels	1159

141.3	SIL Verification Parameters and Results	1161

141.3.1	Sensor Part Configuration	1162

141.3.2	Logic Solver Part Configuration	1164

141.3.3	Final Element Part Configuration	1165

142	SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200	1170

142.1	General SIF Information	1170

142.2	Safety Integrity Levels	1170

142.3	SIL Verification Parameters and Results	1171

142.3.1	Sensor Part Configuration	1172

142.3.2	Logic Solver Part Configuration	1174

142.3.3	Final Element Part Configuration	1175

143	SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001)	1177

143.1	General SIF Information	1177

143.2	Safety Integrity Levels	1177

143.3	SIL Verification Parameters and Results	1178

143.3.1	Sensor Part Configuration	1179

143.3.2	Logic Solver Part Configuration	1181

143.3.3	Final Element Part Configuration	1182

144	SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001)	1184

144.1	General SIF Information	1184

144.2	Safety Integrity Levels	1184

144.3	SIL Verification Parameters and Results	1185

144.3.1	Sensor Part Configuration	1186

144.3.2	Logic Solver Part Configuration	1188

144.3.3	Final Element Part Configuration	1189

145	SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001)	1191

145.1	General SIF Information	1191

145.2	Safety Integrity Levels	1191

145.3	SIL Verification Parameters and Results	1192

145.3.1	Sensor Part Configuration	1193

145.3.2	Logic Solver Part Configuration	1195

145.3.3	Final Element Part Configuration	1196

146	SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001)	1198

146.1	General SIF Information	1198

146.2	Safety Integrity Levels	1198

146.3	SIL Verification Parameters and Results	1199

146.3.1	Sensor Part Configuration	1200

146.3.2	Logic Solver Part Configuration	1202

146.3.3	Final Element Part Configuration	1203

147	SIF-305 SIL1|341TI390 HH => Stop 341HE269	1205

147.1	General SIF Information	1205

147.2	Safety Integrity Levels	1205

147.3	SIL Verification Parameters and Results	1206

147.3.1	Sensor Part Configuration	1207

147.3.2	Logic Solver Part Configuration	1209

147.3.3	Final Element Part Configuration	1210

148	SIF-306 SIL1| Leakage detection 341XI687	1212

148.1	General SIF Information	1212

148.2	Safety Integrity Levels	1212

148.3	SIL Verification Parameters and Results	1213

148.3.1	Sensor Part Configuration	1214

148.3.2	Logic Solver Part Configuration	1217

148.3.3	Final Element Part Configuration	1218

149	SIF-308 SIL1|421PI305 LL => close 421SV501	1223

149.1	General SIF Information	1223

149.2	Safety Integrity Levels	1223

149.3	SIL Verification Parameters and Results	1224

149.3.1	Sensor Part Configuration	1225

149.3.2	Logic Solver Part Configuration	1227

149.3.3	Final Element Part Configuration	1228

150	SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001)	1230

150.1	General SIF Information	1230

150.2	Safety Integrity Levels	1230

150.3	SIL Verification Parameters and Results	1231

150.3.1	Sensor Part Configuration	1232

150.3.2	Logic Solver Part Configuration	1234

150.3.3	Final Element Part Configuration	1235

151	SIF-310 SIL2|421TI304 HH => Stop Compressor (423PU001)	1237

151.1	General SIF Information	1237

151.2	Safety Integrity Levels	1237

151.3	SIL Verification Parameters and Results	1238

151.3.1	Sensor Part Configuration	1239

151.3.2	Logic Solver Part Configuration	1241

151.3.3	Final Element Part Configuration	1242

152	SIF-311 SIL1| 421PI301 > H2 => close 421SV503	1244

152.1	General SIF Information	1244

152.2	Safety Integrity Levels	1244

152.3	SIL Verification Parameters and Results	1245

152.3.1	Sensor Part Configuration	1246

152.3.2	Logic Solver Part Configuration	1248

152.3.3	Final Element Part Configuration	1249

153	SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB	1251

153.1	General SIF Information	1251

153.2	Safety Integrity Levels	1251

153.3	SIL Verification Parameters and Results	1252

153.3.1	Sensor Part Configuration	1253

153.3.2	Logic Solver Part Configuration	1255

153.3.3	Final Element Part Configuration	1256

154	SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB	1258

154.1	General SIF Information	1258

154.2	Safety Integrity Levels	1258

154.3	SIL Verification Parameters and Results	1259

154.3.1	Sensor Part Configuration	1260

154.3.2	Logic Solver Part Configuration	1262

154.3.3	Final Element Part Configuration	1263

155	SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686	1265

155.1	General SIF Information	1265

155.2	Safety Integrity Levels	1265

155.3	SIL Verification Parameters and Results	1266

155.3.1	Sensor Part Configuration	1267

155.3.2	Logic Solver Part Configuration	1269

155.3.3	Final Element Part Configuration	1270

156	SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001)	1272

156.1	General SIF Information	1272

156.2	Safety Integrity Levels	1272

156.3	SIL Verification Parameters and Results	1273

156.3.1	Sensor Part Configuration	1274

156.3.2	Logic Solver Part Configuration	1276

156.3.3	Final Element Part Configuration	1277

157	SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001)	1279

157.1	General SIF Information	1279

157.2	Safety Integrity Levels	1279

157.3	SIL Verification Parameters and Results	1280

157.3.1	Sensor Part Configuration	1281

157.3.2	Logic Solver Part Configuration	1283

157.3.3	Final Element Part Configuration	1284

158	SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) => Stop Compressor (423PU001)	1286

158.1	General SIF Information	1286

158.2	Safety Integrity Levels	1286

158.3	SIL Verification Parameters and Results	1287

158.3.1	Sensor Part Configuration	1288

158.3.2	Logic Solver Part Configuration	1290

158.3.3	Final Element Part Configuration	1291

159	SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001)	1293

159.1	General SIF Information	1293

159.2	Safety Integrity Levels	1293

159.3	SIL Verification Parameters and Results	1294

159.3.1	Sensor Part Configuration	1295

159.3.2	Logic Solver Part Configuration	1297

159.3.3	Final Element Part Configuration	1298

160	SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001)	1300

160.1	General SIF Information	1300

160.2	Safety Integrity Levels	1300

160.3	SIL Verification Parameters and Results	1301

160.3.1	Sensor Part Configuration	1302

160.3.2	Logic Solver Part Configuration	1304

160.3.3	Final Element Part Configuration	1305

161	SIF-320 SIL1 | H2-läckage i kulvert (LKAB) HH (KD184-900)	1307

161.1	General SIF Information	1307

161.2	Safety Integrity Levels	1307

161.3	SIL Verification Parameters and Results	1308

161.3.1	Sensor Part Configuration	1309

161.3.2	Logic Solver Part Configuration	1311

161.3.3	Final Element Part Configuration	1312

162	SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901)	1317

162.1	General SIF Information	1317

162.2	Safety Integrity Levels	1317

162.3	SIL Verification Parameters and Results	1318

162.3.1	Sensor Part Configuration	1319

162.3.2	Logic Solver Part Configuration	1321

162.3.3	Final Element Part Configuration	1322

163	SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910)	1327

163.1	General SIF Information	1327

163.2	Safety Integrity Levels	1327

163.3	SIL Verification Parameters and Results	1328

163.3.1	Sensor Part Configuration	1330

163.3.2	Logic Solver Part Configuration	1331

163.3.3	Final Element Part Configuration	1332

164	SIF-323 SIL1 | H2-läckage övre tunnel HH (KD184-911)	1339

164.1	General SIF Information	1339

164.2	Safety Integrity Levels	1339

164.3	SIL Verification Parameters and Results	1340

164.3.1	Sensor Part Configuration	1342

164.3.2	Logic Solver Part Configuration	1343

164.3.3	Final Element Part Configuration	1344

165	SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913)	1351

165.1	General SIF Information	1351

165.2	Safety Integrity Levels	1351

165.3	SIL Verification Parameters and Results	1352

165.3.1	Sensor Part Configuration	1354

165.3.2	Logic Solver Part Configuration	1355

165.3.3	Final Element Part Configuration	1356

166	SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502	1363

166.1	General SIF Information	1363

166.2	Safety Integrity Levels	1363

166.3	SIL Verification Parameters and Results	1364

166.3.1	Sensor Part Configuration	1365

166.3.2	Logic Solver Part Configuration	1367

166.3.3	Final Element Part Configuration	1367

167	SILver™ Group Reuse Overview	1370

167.1	Sensor Groups Reused	1370

167.2	Logic Solver Groups Reused	1370

167.3	Final Element Groups Reused	1370

168	Abbreviations and Definitions	1373

168.1	Abbreviations	1373

168.2	Definitions	1373

169	Disclaimer, Assumptions, Equipment Data	1375

169.1	Disclaimer	1375

169.2	Assumptions SILver™	1375

169.3	Equipment Data	1375

# Purpose and Scope

This document, automatically generated by the exida exSILentia® software, details the results, selections, and assumptions made during the Safety Integrity Level verification for the Safety Instrumented System (SIS) and its associated Safety Instrumented Functions (SIF) for the Hybrit Pilot Plant project.

## General Project Information

| Project Identification: | 001 |
| --- | --- |
| Project Name: | Hybrit Pilot Plant |
| Revision: | 2020-09-21 Uppdaterat: SIF-24 SIF-83 SIF-84 SIF-85 |
| Company: | Hybrit Development AB |
| Project Description: |  |

# SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning

This chapter details the SIL Verification results, selections, and assumptions for the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Low Pressure (254PI330¦L1) nitrogen system, CO2 cleaning |
| --- | --- |
| SIF Tag | SIF-001 |
| SIF Description: | 254PI330 L1 low pressure on nitrogen close 254SV559 close 254SV561. Open bleed after GSS. |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 684 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.46E-03 | 684 | 2 | 2 | N/A | 16.67 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function is quantified as follows.

Table 2 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.37E-03 | 2 | N/A | 208.72 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low Pressure nitrogen system

The information and reliability data underneath describe the Low Pressure nitrogen system sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low Pressure nitrogen system |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 254PI330 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 254PI330

The following table shows the equipment that defines sensor leg 1-1 254PI330.

Table 3 Sensor Leg 1-1: 254PI330 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 254PI330.

Table 4 Reliability Data Sensor Leg 1-1 254PI330

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function is quantified as follows.

Table 5 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 6 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 7 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning Safety Instrumented Function is quantified as follows.

Table 8 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.25E-05 | 3 | N/A | 267.4 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Nitrogen system

The information and reliability data underneath describe the Nitrogen system final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Nitrogen system |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV559 , 254SV561 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| pr | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV559 , 254SV561

The following table shows the equipment that defines final element leg 1-2 254SV559 , 254SV561.

Table 9 Final Element Leg 1-2: 254SV559 , 254SV561 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VPVL |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV559 , 254SV561.

Table 10 Reliability Data Final Element Leg 1-2 254SV559 , 254SV561

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VPVL | - | 4.25E-08 | - | 8.49E-09 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 79.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system

This chapter details the SIL Verification results, selections, and assumptions for the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system |
| --- | --- |
| SIF Tag | SIF-002 |
| SIF Description: | Low differential pressure 254XI330 (254PI330/ 347PI306) protect nitrogen and close 254SV559 and close 254SV561 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 371.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 11 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.69E-03 | 371.9 | 2 | 2 | N/A | 17.95 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function is quantified as follows.

Table 12 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.60E-03 | 2 | N/A | 2044.67 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low differentialpressure nitrogen system

The information and reliability data underneath describe the Low differentialpressure nitrogen system sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low differentialpressure nitrogen system |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 254PI330, 347PI306 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 254PI330, 347PI306

The following table shows the equipment that defines sensor leg 1-2 254PI330, 347PI306.

Table 13 Sensor Leg 1-2: 254PI330, 347PI306 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 254PI330, 347PI306.

Table 14 Reliability Data Sensor Leg 1-2 254PI330, 347PI306

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function is quantified as follows.

Table 15 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 16 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 17 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system Safety Instrumented Function is quantified as follows.

Table 18 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.25E-05 | 3 | N/A | 267.4 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Nitrogen system

The information and reliability data underneath describe the Nitrogen system final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Nitrogen system |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV559 , 254SV561 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV559 , 254SV561

The following table shows the equipment that defines final element leg 1-2 254SV559 , 254SV561.

Table 19 Final Element Leg 1-2: 254SV559 , 254SV561 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VPVL |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV559 , 254SV561.

Table 20 Reliability Data Final Element Leg 1-2 254SV559 , 254SV561

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VPVL | - | 4.25E-08 | - | 8.49E-09 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 79.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 High level (347LZ302) in Absorber (347YM100) |
| --- | --- |
| SIF Tag | SIF-003 |
| SIF Description: | High level (347LZ302 H1) in absorber (347YM100) close 347SV509 (USY feed water) and stop 346PU101 top gas compressor |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 494 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 21 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.02E-03 | 494 | 2 | 2 | N/A | 18.81 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 22 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.05E-03 | 2 | N/A | 263.52 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High level in Absorber

The information and reliability data underneath describe the High level in Absorber sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High level in Absorber |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LZ302 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 92.2 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LZ302

The following table shows the equipment that defines sensor leg 1-1 347LZ302.

Table 23 Sensor Leg 1-1: 347LZ302 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LZ302.

Table 24 Reliability Data Sensor Leg 1-1 347LZ302

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 81.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 25 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 26 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 27 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 28 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.68E-04 | 2 | N/A | 1162.95 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: USY feed water

The information and reliability data underneath describe the USY feed water final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | USY feed water |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV509 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 347SV509

The following table shows the equipment that defines final element leg 1-1 347SV509.

Table 29 Final Element Leg 1-1: 347SV509 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VPVL |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 347SV509.

Table 30 Reliability Data Final Element Leg 1-1 347SV509

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VPVL | - | 4.25E-08 | - | 8.49E-09 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 79.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: top gas compressor

The information and reliability data underneath describe the top gas compressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | top gas compressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 31 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 32 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Low level (347LZ300) in Absorber (347YM100) |
| --- | --- |
| SIF Tag | SIF-004 |
| SIF Description: | SIL2 Low level (347LZ300) in Absorber (347YM100) stop Rich MEA to Stripper -> 347SV672 close and 347SV673 close |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 764.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 33 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.31E-03 | 764.8 | 2 | 2 | N/A | 18.11 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 34 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.20E-03 | 2 | N/A | 272.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low level in Absorber

The information and reliability data underneath describe the Low level in Absorber sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low level in Absorber |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LZ300 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 91.9 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LZ300

The following table shows the equipment that defines sensor leg 1-1 347LZ300.

Table 35 Sensor Leg 1-1: 347LZ300 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LZ300.

Table 36 Reliability Data Sensor Leg 1-1 347LZ300

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 79.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 37 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 38 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 39 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 40 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.79E-05 | 3 | N/A | 329.73 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: stop Rich MEA to Stripper

The information and reliability data underneath describe the stop Rich MEA to Stripper final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | stop Rich MEA to Stripper |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV672, 347SV673 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 86.7 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 347SV672, 347SV673

The following table shows the equipment that defines final element leg 1-2 347SV672, 347SV673.

Table 41 Final Element Leg 1-2: 347SV672, 347SV673 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| B1J |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 347SV672, 347SV673.

Table 42 Reliability Data Final Element Leg 1-2 347SV672, 347SV673

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| B1J | - | - | - | 2.40E-08 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 74.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101

This chapter details the SIL Verification results, selections, and assumptions for the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 |
| --- | --- |
| SIF Tag | SIF-005 |
| SIF Description: | High level ( 347LS305 H1) filter separator 347SE101 stop 346PU101 (top gas compressor) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 775.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 43 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.29E-03 | 775.8 | 2 | 2 | N/A | 18.8 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function is quantified as follows.

Table 44 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.20E-03 | 2 | N/A | 272.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High level filter separator 347SE101

The information and reliability data underneath describe the High level filter separator 347SE101 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High level filter separator 347SE101 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LS305 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 91.9 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LS305

The following table shows the equipment that defines sensor leg 1-1 347LS305.

Table 45 Sensor Leg 1-1: 347LS305 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LS305.

Table 46 Reliability Data Sensor Leg 1-1 347LS305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 79.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function is quantified as follows.

Table 47 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 48 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 49 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 Safety Instrumented Function is quantified as follows.

Table 50 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.93E-05 | 2 | N/A | 990.65 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Top gas compressor

The information and reliability data underneath describe the Top gas compressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Top gas compressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 51 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 52 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close

This chapter details the SIL Verification results, selections, and assumptions for the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close |
| --- | --- |
| SIF Tag | SIF-006 |
| SIF Description: | Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 369.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 53 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.70E-03 | 369.9 | 2 | 2 | N/A | 18.18 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function is quantified as follows.

Table 54 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.60E-03 | 2 | N/A | 1976.35 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low pressure treated gas

The information and reliability data underneath describe the Low pressure treated gas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low pressure treated gas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347PI306, 347PI311 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 347PI306, 347PI311

The following table shows the equipment that defines sensor leg 1-2 347PI306, 347PI311.

Table 55 Sensor Leg 1-2: 347PI306, 347PI311 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 347PI306, 347PI311.

Table 56 Reliability Data Sensor Leg 1-2 347PI306, 347PI311

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function is quantified as follows.

Table 57 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 58 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 59 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close Safety Instrumented Function is quantified as follows.

Table 60 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.79E-05 | 3 | N/A | 329.73 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: stop Rich MEA to Stripper

The information and reliability data underneath describe the stop Rich MEA to Stripper final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | stop Rich MEA to Stripper |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV672, 347SV673 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 86.7 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 347SV672, 347SV673

The following table shows the equipment that defines final element leg 1-2 347SV672, 347SV673.

Table 61 Final Element Leg 1-2: 347SV672, 347SV673 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| B1J |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 347SV672, 347SV673.

Table 62 Reliability Data Final Element Leg 1-2 347SV672, 347SV673

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| B1J | - | - | - | 2.40E-08 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 74.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps

This chapter details the SIL Verification results, selections, and assumptions for the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps |
| --- | --- |
| SIF Tag | SIF-007 |
| SIF Description: | High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 237.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 63 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.21E-03 | 237.2 | 2 | 2 | N/A | 18.15 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function is quantified as follows.

Table 64 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.25E-03 | 2 | N/A | 491.58 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High Temperature after lean MEA cooler

The information and reliability data underneath describe the High Temperature after lean MEA cooler sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High Temperature after lean MEA cooler |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347TI338 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 91.4 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347TI338

The following table shows the equipment that defines sensor leg 1-1 347TI338.

Table 65 Sensor Leg 1-1: 347TI338 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347TI338.

Table 66 Reliability Data Sensor Leg 1-1 347TI338

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 43.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function is quantified as follows.

Table 67 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 68 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 69 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps Safety Instrumented Function is quantified as follows.

Table 70 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.66E-04 | 2 | N/A | 626.52 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close suction side MEA pumps

The information and reliability data underneath describe the close suction side MEA pumps final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close suction side MEA pumps |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV674 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 86.7 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 347SV674

The following table shows the equipment that defines final element leg 1-1 347SV674.

Table 71 Final Element Leg 1-1: 347SV674 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| B1J |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 347SV674.

Table 72 Reliability Data Final Element Leg 1-1 347SV674

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| B1J | - | - | - | 2.40E-08 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 74.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608

This chapter details the SIL Verification results, selections, and assumptions for the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 |
| --- | --- |
| SIF Tag | SIF-008 |
| SIF Description: | High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 39.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 8 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 73 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.51E-02 | 39.8 | 1 | 2 | N/A | 18.79 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function is quantified as follows.

Table 74 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.05E-03 | 2 | N/A | 263.52 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High level in MEA reboiler

The information and reliability data underneath describe the High level in MEA reboiler sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High level in MEA reboiler |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LZ329 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 92.2 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LZ329

The following table shows the equipment that defines sensor leg 1-1 347LZ329.

Table 75 Sensor Leg 1-1: 347LZ329 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LZ329.

Table 76 Reliability Data Sensor Leg 1-1 347LZ329

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 81.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function is quantified as follows.

Table 77 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.61 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 78 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 79 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 Safety Instrumented Function is quantified as follows.

Table 80 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.40E-02 | 2 | N/A | 1096.4 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 347RV608

The information and reliability data underneath describe the close 347RV608 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 347RV608 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347RV608 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 347RV608

The following table shows the equipment that defines final element leg 1-1 347RV608.

Table 81 Final Element Leg 1-1: 347RV608 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VD |  | - | - | A | 2 |
| Metso GU |  | - | - | A | 2 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 347RV608.

Table 82 Reliability Data Final Element Leg 1-1 347RV608

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VD | - | - | - | 5.60E-07 | - | - | - |
| Metso GU | - | - | - | 1.15E-06 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100) close 347SV671 lean MEA to Absorber

This chapter details the SIL Verification results, selections, and assumptions for the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100) close 347SV671 lean MEA to Absorber |
| --- | --- |
| SIF Tag | SIF-009 |
| SIF Description: | Low differential pressure 347PD339 Pump discharge and absorber (347YM100) Close 347SV671 Lean MEA to Absorber Close 347RV667 lean MEA to Absorber |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 650.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 83 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.54E-03 | 650.5 | 2 | 2 | N/A | 17.04 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function is quantified as follows.

Table 84 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.39E-03 | 2 | N/A | 208.73 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low differential pressure Pump discharge and absorber (347YM100)

The information and reliability data underneath describe the Low differential pressure Pump discharge and absorber (347YM100) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low differential pressure Pump discharge and absorber (347YM100) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347PD339 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347PD339

The following table shows the equipment that defines sensor leg 1-1 347PD339.

Table 85 Sensor Leg 1-1: 347PD339 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347PD339.

Table 86 Reliability Data Sensor Leg 1-1 347PD339

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.89E-08 1.37E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function is quantified as follows.

Table 87 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 88 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 89 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber Safety Instrumented Function is quantified as follows.

Table 90 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-04 | 3 | N/A | 413.74 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close lean MEA to Absorber

The information and reliability data underneath describe the close lean MEA to Absorber final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close lean MEA to Absorber |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV671, 347RV667 |
| Voting within group: | 1oo2 |
| Voting type: | Diverse |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 347SV671

The following table shows the equipment that defines final element leg 1 347SV671.

Table 91 Final Element Leg 1: 347SV671 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| B1J |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 347SV671.

Table 92 Reliability Data Final Element Leg 1 347SV671

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| B1J | - | - | - | 2.40E-08 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 74.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 347RV667

The following table shows the equipment that defines final element leg 2 347RV667.

Table 93 Final Element Leg 2: 347RV667 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VD |  | - | - | A | 2 |
| Metso GU |  | - | - | A | 2 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 347RV667.

Table 94 Reliability Data Final Element Leg 2 347RV667

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VD | - | - | - | 5.60E-07 | - | - | - |
| Metso GU | - | - | - | 1.15E-06 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor (DENNA UTGÅR)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor (DENNA UTGÅR) |
| --- | --- |
| SIF Tag | SIF-010 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 0 with RRF = 0 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 95 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 0.00E+00 | 0 | 0 | 0 | N/A | ∞ |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function is quantified as follows.

Table 96 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | 0 | N/A | ∞ | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low pressure instrument air

The information and reliability data underneath describe the Low pressure instrument air sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low pressure instrument air |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 261PZ330 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 261PZ330

The following table shows the equipment that defines sensor leg 1-1 261PZ330.

Table 97 Sensor Leg 1-1: 261PZ330 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 261PZ330.

Table 98 Reliability Data Sensor Leg 1-1 261PZ330

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
|  |  |  |  |  |  |  | SFF [%] |  |  | 0.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function is quantified as follows.

Table 99 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | - | N/A | ∞ | 0 | 2 |

The information and reliability data underneath describe the  logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: |  |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: |  |
| Proof Test Interval [Months]: |  |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: |  |

Table 100  Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group .

Table 101 Reliability Data Logic Solver Group

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
|  |  |  |  |  | SFF [%] |  | 0.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-010 Low pressure (261PZ330) instrument air stop 346PU101 top gas compressor  (DENNA UTGÅR) Safety Instrumented Function is quantified as follows.

Table 102 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | 0 | N/A | ∞ | 0 | 2 |

| Number of Final Element group(s): | 0 |
| --- | --- |
| Voting between groups: | 0oo0 |
| -factor [%]: | N/A |

# SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H2) |
| --- | --- |
| SIF Tag | SIF-011 |
| SIF Description: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H2) => Open Topptryck nödventil eft. våtelfilter red. gas (345SV599 SIL2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil H2S till PGH (256SV522 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Trip Processgaskompressor (346PU101 SIL2) Close H2 till reduktionskrets (341SV672/341RV675 SIL2) Close NG till reduktionskrets (252SV562/252RV565 SIL2) Close NG till kylkrets (252SV614/252RV618 SIL2) Close N2 till kylkrets (254SV594/254RV595 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Close avstängningsventil N2 till reaktortopp (253SV607 SIL2) Open Avstängningsventiler venturi reduktionsgas (345SV520/21/22 SIL2) Open Avstängningsventiler venturi processgas (353SV520/21/22 SIL2) Close H2 processgaskrets (341SV881) Close CO processgaskrets (356SV511) Stop P4 värmare 344HE002 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 373.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 103 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.67E-03 | 373.9 | 2 | 2 | N/A | 36.73 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function is quantified as follows.

Table 104 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.04E-05 | 3 | N/A | 3312.46 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck toppgas

The information and reliability data underneath describe the Gastryck toppgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck toppgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ321, 320PZ322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 105 Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 106 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ321, 320PZ322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function is quantified as follows.

Table 107 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.76E-06 | 2 | N/A | 37.72 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 108 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 109 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2) Safety Instrumented Function is quantified as follows.

Table 110 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.62E-03 | 2 | N/A | 2425.2 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Final Element Group 1: Beräkning av SIF-011 "open"

The information and reliability data underneath describe the Beräkning av SIF-011 "open" final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Beräkning av SIF-011 "open" |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Beräkning av SIF-011 "open" |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 100 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: Beräkning av SIF-011 "open"

The following table shows the equipment that defines final element leg 1-1 Beräkning av SIF-011 "open".

Table 111 Final Element Leg 1-1: Beräkning av SIF-011 "open" Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Beräkning av SIF-011 Open |  | - | - | A | 2 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Beräkning av SIF-011 "open".

Table 112 Reliability Data Final Element Leg 1-1 Beräkning av SIF-011 "open"

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Beräkning av SIF-011 Open | - | 1.01E-07 | - | 2.85E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 41.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Beräkning av SIF-011 "close"

The information and reliability data underneath describe the Beräkning av SIF-011 "close" final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Beräkning av SIF-011 "close" |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Beräkning av SIF-011 "close" |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 100 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: Beräkning av SIF-011 "close"

The following table shows the equipment that defines final element leg 1-1 Beräkning av SIF-011 "close".

Table 113 Final Element Leg 1-1: Beräkning av SIF-011 "close" Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Beräkning av SIF-011 Close |  | - | - | A | 2 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Beräkning av SIF-011 "close".

Table 114 Reliability Data Final Element Leg 1-1 Beräkning av SIF-011 "close"

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Beräkning av SIF-011 Close | - | 4.77E-11 | - | 7.47E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 12.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-011 Beräkning av SIF-011 "open"

This chapter details the SIL Verification results, selections, and assumptions for the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Beräkning av SIF-011 "open" |
| --- | --- |
| SIF Tag | SIF-011 |
| SIF Description: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H2) => Open Topptryck nödventil eft. våtelfilter red. gas (345SV599 SIL2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil H2S till PGH (256SV522 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Trip Processgaskompressor (346PU101 SIL2) Close H2 till reduktionskrets (341SV672/341RV675 SIL2) Close NG till reduktionskrets (252SV562/252RV565 SIL2) Close NG till kylkrets (252SV614/252RV618 SIL2) Close N2 till kylkrets (254SV594/254RV595 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Close avstängningsventil N2 till reaktortopp (253SV607 SIL2) Open Avstängningsventiler venturi reduktionsgas (345SV520/21/22 SIL2) Open Avstängningsventiler venturi processgas (353SV520/21/22 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 0 with RRF = 0 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 3 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 115 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 0.00E+00 | 0 | 0 | 0 | N/A | ∞ |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function is quantified as follows.

Table 116 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | 0 | N/A | ∞ | 0 | 2 |

| Number of Sensor group(s): | 0 |
| --- | --- |
| Voting between groups: | 0oo0 |
| -factor [%]: | N/A |

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function is quantified as follows.

Table 117 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | - | N/A | ∞ | 0 | 2 |

The information and reliability data underneath describe the  logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: |  |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: |  |
| Proof Test Interval [Months]: |  |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: |  |

Table 118  Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group .

Table 119 Reliability Data Logic Solver Group

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
|  |  |  |  |  | SFF [%] |  | 0.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-011 Beräkning av SIF-011 "open" Safety Instrumented Function is quantified as follows.

Table 120 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.25E-03 | 3 | N/A | 1131.76 | 1 | 3 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Final Element Group 1: Open 345SV599 & 345SV524

The information and reliability data underneath describe the Open 345SV599 & 345SV524 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open 345SV599 & 345SV524 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV599, 345SV524 |
| Voting within group: | 1oo2 |
| Voting type: | Diverse |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 6 |
| Proof Test Coverage [%]: | 89.3 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 345SV599

The following table shows the equipment that defines final element leg 1 345SV599.

Table 121 Final Element Leg 1: 345SV599 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 345SV599.

Table 122 Reliability Data Final Element Leg 1 345SV599

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 3.70E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 5.1 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 345SV524

The following table shows the equipment that defines final element leg 2 345SV524.

Table 123 Final Element Leg 2: 345SV524 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 345SV524.

Table 124 Reliability Data Final Element Leg 2 345SV524

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 6.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Open Avstängningsventiler venturi reduktionsgas

The information and reliability data underneath describe the Open Avstängningsventiler venturi reduktionsgas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open Avstängningsventiler venturi reduktionsgas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV520, 345SV521, 345SV522 |
| Voting within group: | 1oo3 |
| Voting type: | Diverse |
| HFT: | 2 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 6 |
| Proof Test Coverage [%]: | 84.1 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 345SV520

The following table shows the equipment that defines final element leg 1 345SV520.

Table 125 Final Element Leg 1: 345SV520 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 345SV520.

Table 126 Reliability Data Final Element Leg 1 345SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 6.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 345SV521

The following table shows the equipment that defines final element leg 2 345SV521.

Table 127 Final Element Leg 2: 345SV521 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 345SV521.

Table 128 Reliability Data Final Element Leg 2 345SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 6.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 3: 345SV522

The following table shows the equipment that defines final element leg 3 345SV522.

Table 129 Final Element Leg 3: 345SV522 Details

| Final ELement Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 3 345SV522.

Table 130 Reliability Data Final Element Leg 3 345SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | 1.46E-07 | - | 3.22E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 17.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-011 Beräkning av SIF-011 "close"

This chapter details the SIL Verification results, selections, and assumptions for the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Beräkning av SIF-011 "close" |
| --- | --- |
| SIF Tag | SIF-011 |
| SIF Description: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H2) => Open Topptryck nödventil eft. våtelfilter red. gas (345SV599 SIL2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil H2S till PGH (256SV522 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Trip Processgaskompressor (346PU101 SIL2) Close H2 till reduktionskrets (341SV672/341RV675 SIL2) Close NG till reduktionskrets (252SV562/252RV565 SIL2) Close NG till kylkrets (252SV614/252RV618 SIL2) Close N2 till kylkrets (254SV594/254RV595 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Close avstängningsventil N2 till reaktortopp (253SV607 SIL2) Open Avstängningsventiler venturi reduktionsgas (345SV520/21/22 SIL2) Open Avstängningsventiler venturi processgas (353SV520/21/22 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 0 with RRF = 0 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 3 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 131 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 0.00E+00 | 0 | 0 | 0 | N/A | ∞ |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function is quantified as follows.

Table 132 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | 0 | N/A | ∞ | 0 | 2 |

| Number of Sensor group(s): | 0 |
| --- | --- |
| Voting between groups: | 0oo0 |
| -factor [%]: | N/A |

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function is quantified as follows.

Table 133 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 0.00E+00 | - | N/A | ∞ | 0 | 2 |

The information and reliability data underneath describe the  logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: |  |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: |  |
| Proof Test Interval [Months]: |  |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: |  |

Table 134  Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group .

Table 135 Reliability Data Logic Solver Group

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
|  |  |  |  |  | SFF [%] |  | 0.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-011 Beräkning av SIF-011 "close" Safety Instrumented Function is quantified as follows.

Table 136 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.27E-03 | 3 | N/A | 23908.06 | 1 | 3 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: SIF-011 Close 2oo3

The information and reliability data underneath describe the SIF-011 Close 2oo3 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIF-011 Close 2oo3 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV562, 341SV672 , 253SV607 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 6 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-3: 252SV562, 341SV672 , 253SV607

The following table shows the equipment that defines final element leg 1-3 252SV562, 341SV672 , 253SV607.

Table 137 Final Element Leg 1-3: 252SV562, 341SV672 , 253SV607 Details

| Final ELement Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-3 252SV562, 341SV672 , 253SV607.

Table 138 Reliability Data Final Element Leg 1-3 252SV562, 341SV672 , 253SV607

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 5.1 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: SIF-011 Close 2oo4

The information and reliability data underneath describe the SIF-011 Close 2oo4 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIF-011 Close 2oo4 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV582, 271SV556, 256SV522, 251SV561 |
| Voting within group: | 2oo4 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 6 |
| Proof Test Coverage [%]: | 82.9 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-4: 254SV582, 271SV556, 256SV522, ...

The following table shows the equipment that defines final element leg 1-4 254SV582, 271SV556, 256SV522, ....

Table 139 Final Element Leg 1-4: 254SV582, 271SV556, 256SV522, ... Details

| Final ELement Leg 1-4 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-4 254SV582, 271SV556, 256SV522, ....

Table 140 Reliability Data Final Element Leg 1-4 254SV582, 271SV556, 256SV522, ...

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 5.1 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: SIF-011 Close 1oo2

The information and reliability data underneath describe the SIF-011 Close 1oo2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIF-011 Close 1oo2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 82.9 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 141 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 142 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 4.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦L2) |
| --- | --- |
| SIF Tag | SIF-012 |
| SIF Description: | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦L2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 148.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 3 Logic Solver: SSI 3 Final Elements: SSI 3 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 143 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.74E-03 | 148.3 | 2 | 2 | N/A | 36.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function is quantified as follows.

Table 144 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.31E-05 | 3 | N/A | 3341.86 | 1 | 3 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck toppgas

The information and reliability data underneath describe the Gastryck toppgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck toppgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ321, 320PZ322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 145 Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 146 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ321, 320PZ322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function is quantified as follows.

Table 147 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.46E-06 | 2 | N/A | 37.72 | 0 | 3 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 148 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 149 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2) Safety Instrumented Function is quantified as follows.

Table 150 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.69E-03 | 2 | N/A | 2004.76 | 0 | 3 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: Open N2 till reduktionskrets

The information and reliability data underneath describe the Open N2 till reduktionskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open N2 till reduktionskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV582 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 254SV582

The following table shows the equipment that defines final element leg 1-1 254SV582.

Table 151 Final Element Leg 1-1: 254SV582 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV582.

Table 152 Reliability Data Final Element Leg 1-1 254SV582

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängning O2

The information and reliability data underneath describe the Avstängning O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 153 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker Lucifer N-Series | 2008.3.03 | - | - | A | - |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 154 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker Lucifer N-Series | - | 1.53E-07 | - | 9.93E-07 | - | - | 1.45E-06 |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 8.1 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Avstängningsventil 2 överhettad ånga till PGH PT 6

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH PT 6 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH PT 6 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 155 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 156 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H3) |
| --- | --- |
| SIF Tag | SIF-013 |
| SIF Description: | Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H3) => Open nödventil eft. spraykylare (345SV524 & 353SV524) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 57.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 157 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.73E-02 | 57.8 | 1 | 2 | N/A | 16.73 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function is quantified as follows.

Table 158 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.05E-04 | 3 | N/A | 1698.47 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck toppgas

The information and reliability data underneath describe the Gastryck toppgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck toppgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ321, 320PZ322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 159 Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 160 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ321, 320PZ322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function is quantified as follows.

Table 161 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.49E-06 | 2 | N/A | 16.94 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 162 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 163 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3) Safety Instrumented Function is quantified as follows.

Table 164 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.72E-02 | 2 | N/A | 7069.74 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open Topptryck nödventil eft. spraykylare red. gas

The information and reliability data underneath describe the Open Topptryck nödventil eft. spraykylare red. gas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open Topptryck nödventil eft. spraykylare red. gas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV524, 353SV524 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 345SV524, 353SV524

The following table shows the equipment that defines final element leg 1-2 345SV524, 353SV524.

Table 165 Final Element Leg 1-2: 345SV524, 353SV524 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 345SV524, 353SV524.

Table 166 Reliability Data Final Element Leg 1-2 345SV524, 353SV524

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 55.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325¦H2) |
| --- | --- |
| SIF Tag | SIF-015 |
| SIF Description: | SIL1 Temp toppgas (320TZ323, 320TZ324 & 320TZ325¦H2) => Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2 ) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Trip 344HE002 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 175.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 167 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.69E-03 | 175.6 | 2 | 2 | N/A | 16.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function is quantified as follows.

Table 168 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.31E-04 | 3 | N/A | 1693.48 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp toppgas

The information and reliability data underneath describe the Temp toppgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp toppgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320TZ323, 320TZ324, 320TZ325 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 320TZ323, 320TZ324, 320TZ325

The following table shows the equipment that defines sensor leg 1-3 320TZ323, 320TZ324, 320TZ325.

Table 169 Sensor Leg 1-3: 320TZ323, 320TZ324, 320TZ325 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | ü | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320TZ323, 320TZ324, 320TZ325.

Table 170 Reliability Data Sensor Leg 1-3 320TZ323, 320TZ324, 320TZ325

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function is quantified as follows.

Table 171 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 172 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 173 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2) Safety Instrumented Function is quantified as follows.

Table 174 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.55E-03 | 2 | N/A | 1170.68 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: O2 inj

The information and reliability data underneath describe the O2 inj final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 inj |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 175 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 176 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: NG till brännare PGH

The information and reliability data underneath describe the NG till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 177 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 178 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 179 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 180 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-016 SIL1 Temp överhettad ånga (271TI552|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temp överhettad ånga (271TI552¦L2) |
| --- | --- |
| SIF Tag | SIF-016 |
| SIF Description: | SIL1 Temp överhettad ånga (271TI552¦L2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 106.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 181 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 9.38E-03 | 106.6 | 2 | 2 | N/A | 18.29 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function is quantified as follows.

Table 182 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-03 | 2 | N/A | 554.98 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp överhettad ånga

The information and reliability data underneath describe the Temp överhettad ånga sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp överhettad ånga |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 271TI552 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 271TI552

The following table shows the equipment that defines sensor leg 1-1 271TI552.

Table 183 Sensor Leg 1-1: 271TI552 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 271TI552.

Table 184 Reliability Data Sensor Leg 1-1 271TI552

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function is quantified as follows.

Table 185 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 186 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 187 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-016 SIL1 Temp överhettad ånga (271TI552|L2) Safety Instrumented Function is quantified as follows.

Table 188 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 189 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 190 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Tryck överhettad ånga (271PI552¦L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |
| --- | --- |
| SIF Tag | SIF-017 |
| SIF Description: | SIL1 Tryck överhettad ånga (271PI552¦L2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 114 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 191 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.77E-03 | 114 | 2 | 2 | N/A | 17.73 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 192 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.86E-04 | 2 | N/A | 284.42 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck överhettad ånga

The information and reliability data underneath describe the Tryck överhettad ånga sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck överhettad ånga |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 271PI552 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 271PI552

The following table shows the equipment that defines sensor leg 1-1 271PI552.

Table 193 Sensor Leg 1-1: 271PI552 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 271PI552.

Table 194 Reliability Data Sensor Leg 1-1 271PI552

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 195 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 196 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 197 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 198 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 199 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 200 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |
| --- | --- |
| SIF Tag | SIF-018 |
| SIF Description: | SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) => Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 108.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 201 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 9.20E-03 | 108.7 | 2 | 2 | N/A | 18.89 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 202 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.22E-03 | 2 | N/A | 13413.9 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Tryck överhettad ånga friblåsning

The information and reliability data underneath describe the Tryck överhettad ånga friblåsning sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck överhettad ånga friblåsning |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 271PI320 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 271PI320

The following table shows the equipment that defines sensor leg 1-1 271PI320.

Table 203 Sensor Leg 1-1: 271PI320 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 271PI320.

Table 204 Reliability Data Sensor Leg 1-1 271PI320

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Tryck överhettad ånga friblåsning

The information and reliability data underneath describe the Tryck överhettad ånga friblåsning sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck överhettad ånga friblåsning |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PZ305, 343PZ307, 343PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308

The following table shows the equipment that defines sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 205 Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 206 Reliability Data Sensor Leg 1-3 343PZ305, 343PZ307, 343PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 5.21E-08 | - - | 6.53E-08 4.61E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 15.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 207 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 208 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 209 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Safety Instrumented Function is quantified as follows.

Table 210 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 211 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 212 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Flöde reduktionsgas till PGH (343XI302¦L2) |
| --- | --- |
| SIF Tag | SIF-019 |
| SIF Description: | SIL2 Flöde reduktionsgas till PGH (343XI302¦L2) => Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Endast 1 bränsle åt gången. |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 201.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 213 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.95E-03 | 201.8 | 2 | 2 | N/A | 36.56 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function is quantified as follows.

Table 214 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.28E-03 | 2 | N/A | 5696.55 | 0 | 2 |

| Number of Sensor group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Sensor Group 1: Difftryck

The information and reliability data underneath describe the Difftryck sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Difftryck |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PD302, 343PD303, 343PD304 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 343PD302, 343PD303, 343PD304

The following table shows the equipment that defines sensor leg 1-3 343PD302, 343PD303, 343PD304.

Table 215 Sensor Leg 1-3: 343PD302, 343PD303, 343PD304 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PD302, 343PD303, 343PD304.

Table 216 Reliability Data Sensor Leg 1-3 343PD302, 343PD303, 343PD304

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.89E-08 1.37E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Tryck

The information and reliability data underneath describe the Tryck sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PZ305, 343PZ307, 343PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308

The following table shows the equipment that defines sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 217 Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 218 Reliability Data Sensor Leg 1-3 343PZ305, 343PZ307, 343PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 3: Temperatur

The information and reliability data underneath describe the Temperatur sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperatur |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343TI306 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 343TI306

The following table shows the equipment that defines sensor leg 1-1 343TI306.

Table 219 Sensor Leg 1-1: 343TI306 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 343TI306.

Table 220 Reliability Data Sensor Leg 1-1 343TI306

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.08E-07 | - - | 1.07E-07 1.99E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 40.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function is quantified as follows.

Table 221 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.79E-06 | 2 | N/A | 37.91 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 222 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 223 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2) Safety Instrumented Function is quantified as follows.

Table 224 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.68E-03 | 3 | N/A | 1252.89 | 1 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: H2 till brännare PGH

The information and reliability data underneath describe the H2 till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2 till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV665, 341SV667 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 341SV665, 341SV667

The following table shows the equipment that defines final element leg 1-2 341SV665, 341SV667.

Table 225 Final Element Leg 1-2: 341SV665, 341SV667 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 341SV665, 341SV667.

Table 226 Reliability Data Final Element Leg 1-2 341SV665, 341SV667

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: NG till brännare PGH

The information and reliability data underneath describe the NG till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 227 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 228 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: O2 inj

The information and reliability data underneath describe the O2 inj final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 inj |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 229 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 230 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-020 SIL2 Difftryck O2-transferline (251XI313)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Difftryck O2-transferline (251XI313) |
| --- | --- |
| SIF Tag | SIF-020 |
| SIF Description: | SIL2 Gastryck transferline (251XI313) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Open Avluftningsventil O2 (F.O) (251SV557 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 339 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 231 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.95E-03 | 339 | 2 | 2 | N/A | 16.24 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function is quantified as follows.

Table 232 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.06E-04 | 2 | N/A | 1895.34 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Tryckvakt O2-inj

The information and reliability data underneath describe the Tryckvakt O2-inj sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt O2-inj |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251PZ312, 251PZ313, 251PZ314 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314

The following table shows the equipment that defines sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 233 Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 234 Reliability Data Sensor Leg 1-3 251PZ312, 251PZ313, 251PZ314

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Gastryck transferline

The information and reliability data underneath describe the Gastryck transferline sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck transferline |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344PZ321 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344PZ321

The following table shows the equipment that defines sensor leg 1-1 344PZ321.

Table 235 Sensor Leg 1-1: 344PZ321 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344PZ321.

Table 236 Reliability Data Sensor Leg 1-1 344PZ321

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function is quantified as follows.

Table 237 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 238 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 239 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-020 SIL2 Difftryck O2-transferline (251XI313) Safety Instrumented Function is quantified as follows.

Table 240 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 241 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 242 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-021 SIL1 Gastryck transferline (344PZ321|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Gastryck transferline (344PZ321¦L2) |
| --- | --- |
| SIF Tag | SIF-021 |
| SIF Description: | SIL1 Gastryck transferline (344PZ321¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 353.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 243 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.83E-03 | 353.6 | 2 | 2 | N/A | 17.35 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function is quantified as follows.

Table 244 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.86E-04 | 2 | N/A | 284.42 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck transferline

The information and reliability data underneath describe the Gastryck transferline sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck transferline |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344PZ321 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344PZ321

The following table shows the equipment that defines sensor leg 1-1 344PZ321.

Table 245 Sensor Leg 1-1: 344PZ321 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344PZ321.

Table 246 Reliability Data Sensor Leg 1-1 344PZ321

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function is quantified as follows.

Table 247 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 248 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 249 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-021 SIL1 Gastryck transferline (344PZ321|L2) Safety Instrumented Function is quantified as follows.

Table 250 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 251 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 252 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryckvakt O2-inj (251XI312 ¦L2) |
| --- | --- |
| SIF Tag | SIF-022 |
| SIF Description: | SIL2 Tryckvakt O2-inj (251XI312 ¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 461.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 253 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.17E-03 | 461.7 | 2 | 2 | N/A | 16.24 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function is quantified as follows.

Table 254 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.20E-04 | 3 | N/A | 1857.58 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryckvakt O2-inj

The information and reliability data underneath describe the Tryckvakt O2-inj sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt O2-inj |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251PZ312, 251PZ313, 251PZ314 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314

The following table shows the equipment that defines sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 255 Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 256 Reliability Data Sensor Leg 1-3 251PZ312, 251PZ313, 251PZ314

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function is quantified as follows.

Table 257 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 258 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 259 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2) Safety Instrumented Function is quantified as follows.

Table 260 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 261 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 262 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Flödesmätare O2 inj (251XI554¦L2) |
| --- | --- |
| SIF Tag | SIF-023 |
| SIF Description: | SIL2 Flödesmätare O2 inj (251XI554¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Open Avluftningsventil O2 (F.O) (251SV557 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 235.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 263 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.24E-03 | 235.6 | 2 | 2 | N/A | 16.24 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function is quantified as follows.

Table 264 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.20E-03 | 2 | N/A | 1971.41 | 0 | 2 |

| Number of Sensor group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Sensor Group 1: Tryckvakt O2-inj

The information and reliability data underneath describe the Tryckvakt O2-inj sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt O2-inj |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251PZ312, 251PZ313, 251PZ314 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314

The following table shows the equipment that defines sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 265 Sensor Leg 1-3: 251PZ312, 251PZ313, 251PZ314 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 251PZ312, 251PZ313, 251PZ314.

Table 266 Reliability Data Sensor Leg 1-3 251PZ312, 251PZ313, 251PZ314

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: 251PD554

The information and reliability data underneath describe the 251PD554 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 251PD554 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251PD554 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 251PD554

The following table shows the equipment that defines sensor leg 1-1 251PD554.

Table 267 Sensor Leg 1-1: 251PD554 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 251PD554.

Table 268 Reliability Data Sensor Leg 1-1 251PD554

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 3: 251TI554

The information and reliability data underneath describe the 251TI554 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 251TI554 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251TI554 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 251TI554

The following table shows the equipment that defines sensor leg 1-1 251TI554.

Table 269 Sensor Leg 1-1: 251TI554 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 251TI554.

Table 270 Reliability Data Sensor Leg 1-1 251TI554

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function is quantified as follows.

Table 271 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 272 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 273 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2) Safety Instrumented Function is quantified as follows.

Table 274 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 275 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 276 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Beräkning difftryck 253XI364¦L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) |
| --- | --- |
| SIF Tag | SIF-024 |
| SIF Description: | SIL2 Beräkning difftryck 253XI364 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 340.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 277 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.94E-03 | 340.7 | 2 | 2 | N/A | 18.3 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 278 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.94E-04 | 2 | N/A | 1886.25 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: Difftryck N2

The information and reliability data underneath describe the Difftryck N2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Difftryck N2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ362, 253PZ363, 253PZ364 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364

The following table shows the equipment that defines sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 279 Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 280 Reliability Data Sensor Leg 1-3 253PZ362, 253PZ363, 253PZ364

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Gastryck transferline

The information and reliability data underneath describe the Gastryck transferline sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck transferline |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344PZ321 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344PZ321

The following table shows the equipment that defines sensor leg 1-1 344PZ321.

Table 281 Sensor Leg 1-1: 344PZ321 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344PZ321.

Table 282 Reliability Data Sensor Leg 1-1 344PZ321

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 283 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 284 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 285 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 286 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 287 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 288 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦H2) |
| --- | --- |
| SIF Tag | SIF-025 |
| SIF Description: | SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦H2) => Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2 ) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 213.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 289 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.69E-03 | 213.4 | 2 | 2 | N/A | 19.08 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function is quantified as follows.

Table 290 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.62E-04 | 3 | N/A | 14107.8 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp transferline PT 12

The information and reliability data underneath describe the Gastemp transferline PT 12 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp transferline PT 12 |
| --- | --- |
| Group Description: | SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦L2) |
| Sensor Legs: | 344TZ316, 344TZ317, 344TZ318 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344TZ316, 344TZ317, 344TZ318

The following table shows the equipment that defines sensor leg 1-3 344TZ316, 344TZ317, 344TZ318.

Table 291 Sensor Leg 1-3: 344TZ316, 344TZ317, 344TZ318 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | ü | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ316, 344TZ317, 344TZ318.

Table 292 Reliability Data Sensor Leg 1-3 344TZ316, 344TZ317, 344TZ318

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 4.90E-08 | - - | 2.70E-08 4.02E-07 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 20.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function is quantified as follows.

Table 293 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 294 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 295 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2) Safety Instrumented Function is quantified as follows.

Table 296 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.92E-03 | 2 | N/A | 1169.11 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 297 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 298 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 299 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 300 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: NG till brännare PGH PT12

The information and reliability data underneath describe the NG till brännare PGH PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 301 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 302 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦L2) |
| --- | --- |
| SIF Tag | SIF-026 |
| SIF Description: | SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 3 with RRF ≥ 1000 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 3 with RRF = 1144.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 303 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.73E-04 | 1144.8 | 3 | 3 | N/A | 114.14 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function is quantified as follows.

Table 304 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.15E-05 | 3 | N/A | 3591.84 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp transferline

The information and reliability data underneath describe the Gastemp transferline sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp transferline |
| --- | --- |
| Group Description: | SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦L2) |
| Sensor Legs: | 344TZ316, 344TZ317, 344TZ318 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Beta Estimator Selections

The following selections were made as part of the beta estimator for the Gastemp transferline sensor group.

| Separation/Segregation |  |
| --- | --- |
| Description | Yes/No |
| Are all signal cables for the channels routed separately at all positions? | No |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel on separate printed-circuit boards? | Yes |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel indoors and in separate cabinets? | No |
| Diversity/Redundancy |  |
| Description | Yes/No |
| Do the devices employ different physical principles for the sensing elements for example, pressure and temperature, vane anemometer and Doppler transducer, etc? | No |
| Do the devices employ different electrical principles/designs for example, digital and analogue, different manufacturer (not re-badged) or different technology? | No |
| Are separate test methods and people used for each channel during commissioning? | No |
| Is maintenance on each channel carried out by different people at different times? | No |
| Complexity/Design/Application/Maturity/Experience |  |
| Description | Yes/No |
| Does cross-connection between channels preclude the exchange of any information other than that used for diagnostic testing or voting purposes? | Yes |
| Is the design based on techniques used in equipment that has been used successfully in the field for > 5 years? | Yes |
| Is there more than 5 years experience with the same hardware used in similar environments? | Yes |
| Are inputs and outputs protected from potential levels of over-voltage and over-current? | Yes |
| Are all devices/components conservatively rated (for example, by a factor of 2 or more)? | No |
| Assessment/Analysis and Feedback of Data |  |
| Description | Yes/No |
| Have the results of the failure modes and effects analysis or fault-tree analysis been examined to establish sources of common cause failure and have predetermined sources of common cause failure been eliminated by design? | Yes |
| Were common cause failures considered in design reviews with the results fed back into the design? (Documentary evidence of the design review activity is required.) | No |
| Are all field failures fully analyzed with feedback into the design? (Documentary evidence of the procedure is required.) | No |
| Procedures/Human Interface |  |
| Description | Yes/No |
| Is there a written system of work to ensure that all component failures (or degradations) are detected, the root causes established and other similar items inspected for similar potential causes of failure? | No |
| Are procedures in place to ensure that: maintenance (including adjustment or calibration) of any part of the independent channels is staggered, and, in addition to the manual checks carried out following maintenance, the diagnostic tests are allowed to run satisfactorily between the completion of maintenance on one channel and the start of maintenance on another? | No |
| Do the documented maintenance procedures specify that all parts of redundant systems (for example, cables, etc.) intended to be independent of each other, are not to be relocated? | No |
| Is all maintenance of printed-circuit boards, etc. carried out off-site at a qualified repair centre and have all the repaired items gone through a full pre-installation testing? | No |
| Do the system diagnostic tests report failures to the level of a field-replaceable module? | No |
| Competence/Training/Safety Culture |  |
| Description | Yes/No |
| Have designers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Have maintainers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Environmental Control |  |
| Description | Yes/No |
| Is personnel access limited (for example locked cabinets, inaccessible position)? | Yes |
| Is the system likely to operate always within the range of temperature, humidity, corrosion, dust, vibration, etc., over which it has been tested, without the use of external environmental control? | Yes |
| Are all signal and power cables separate at all positions? | Yes |
| Environmental Testing |  |
| Description | Yes/No |
| Has the system been tested for immunity to all relevant environmental influences (for example EMC, temperature, vibration, shock, humidity) to an appropriate level as specified in recognized standards? | Yes |

##### Sensor Leg 1-3: 344TZ316, 344TZ317, 344TZ318

The following table shows the equipment that defines sensor leg 1-3 344TZ316, 344TZ317, 344TZ318.

Table 305 Sensor Leg 1-3: 344TZ316, 344TZ317, 344TZ318 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | ü | B | - |
| ABB AC800M High Integrity SIL3 [AnalogIn] | 2013.1.02 | - | - | B | 3 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ316, 344TZ317, 344TZ318.

Table 306 Reliability Data Sensor Leg 1-3 344TZ316, 344TZ317, 344TZ318

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - 4.07E-07 | - - | - 1.70E-08 | 2.70E-08 2.70E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL3 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function is quantified as follows.

Table 307 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.76E-08 | 3 | N/A | 140.5 | 1 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL3 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL3 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 1 |
| -factor [%]: | 1 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 308 ABB AC800M High Integrity SIL3 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL3 | 2013.1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL3.

Table 309 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL3

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/TP830 SM811/TP868 (SM810/P855) | 4.51E-07 | 7.54E-07 | 1.46E-06 | 5.56E-11 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: 1*SD821 + 1*SS823 + 2*MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2) Safety Instrumented Function is quantified as follows.

Table 310 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.62E-04 | 3 | N/A | 732.5 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning-O2

The information and reliability data underneath describe the Avstängning-O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning-O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 311 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 2013.1.02 | - | - | B | 3 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 312 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦H2) |
| --- | --- |
| SIF Tag | SIF-027 |
| SIF Description: | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2 ) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 255.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 313 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.92E-03 | 255.3 | 2 | 2 | N/A | 18.6 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function is quantified as follows.

Table 314 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.77E-05 | 3 | N/A | 1878.24 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperatur konvektionsdel

The information and reliability data underneath describe the Temperatur konvektionsdel sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperatur konvektionsdel |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TZ303, 344TZ304, 344TZ305 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344TZ303, 344TZ304, 344TZ305

The following table shows the equipment that defines sensor leg 1-3 344TZ303, 344TZ304, 344TZ305.

Table 315 Sensor Leg 1-3: 344TZ303, 344TZ304, 344TZ305 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ303, 344TZ304, 344TZ305.

Table 316 Reliability Data Sensor Leg 1-3 344TZ303, 344TZ304, 344TZ305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function is quantified as follows.

Table 317 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 318 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 319 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2) Safety Instrumented Function is quantified as follows.

Table 320 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.84E-03 | 3 | N/A | 566.9 | 1 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: NG till brännare PGH PT12

The information and reliability data underneath describe the NG till brännare PGH PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 321 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 322 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 323 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 324 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦L2) |
| --- | --- |
| SIF Tag | SIF-028 |
| SIF Description: | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦L2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 124 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | Yes |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 325 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.06E-03 | 124 | 2 | 2 | 2 | 18.72 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function is quantified as follows.

Table 326 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.77E-05 | 3 | 3 | 1878.24 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperatur konvektionsdel

The information and reliability data underneath describe the Temperatur konvektionsdel sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperatur konvektionsdel |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TZ303, 344TZ304, 344TZ305 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344TZ303, 344TZ304, 344TZ305

The following table shows the equipment that defines sensor leg 1-3 344TZ303, 344TZ304, 344TZ305.

Table 327 Sensor Leg 1-3: 344TZ303, 344TZ304, 344TZ305 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ303, 344TZ304, 344TZ305.

Table 328 Reliability Data Sensor Leg 1-3 344TZ303, 344TZ304, 344TZ305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function is quantified as follows.

Table 329 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | 2 | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 330 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | 2 |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 331 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2) Safety Instrumented Function is quantified as follows.

Table 332 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | 3 | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 333 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 334 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312¦H2) |
| --- | --- |
| SIF Tag | SIF-029 |
| SIF Description: | SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2 ) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 255.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 335 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.92E-03 | 255.3 | 2 | 2 | N/A | 18.6 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function is quantified as follows.

Table 336 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.77E-05 | 3 | N/A | 1878.24 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperatur strålningssdel H2

The information and reliability data underneath describe the Temperatur strålningssdel H2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperatur strålningssdel H2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TZ310, 344TZ311, 344TZ312 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344TZ310, 344TZ311, 344TZ312

The following table shows the equipment that defines sensor leg 1-3 344TZ310, 344TZ311, 344TZ312.

Table 337 Sensor Leg 1-3: 344TZ310, 344TZ311, 344TZ312 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ310, 344TZ311, 344TZ312.

Table 338 Reliability Data Sensor Leg 1-3 344TZ310, 344TZ311, 344TZ312

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function is quantified as follows.

Table 339 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 340 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 341 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2) Safety Instrumented Function is quantified as follows.

Table 342 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.84E-03 | 3 | N/A | 566.9 | 1 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 343 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 344 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: NG till brännare PGH PT12

The information and reliability data underneath describe the NG till brännare PGH PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 345 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 346 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308¦H2) |
| --- | --- |
| SIF Tag | SIF-031 |
| SIF Description: | SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 252.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 347 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.96E-03 | 252.6 | 2 | 2 | N/A | 16.46 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function is quantified as follows.

Table 348 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.08E-04 | 3 | N/A | 1776.27 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck förbränningskammare

The information and reliability data underneath describe the Tryck förbränningskammare sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck förbränningskammare |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344PZ306, 344PZ307, 344PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344PZ306, 344PZ307, 344PZ308

The following table shows the equipment that defines sensor leg 1-3 344PZ306, 344PZ307, 344PZ308.

Table 349 Sensor Leg 1-3: 344PZ306, 344PZ307, 344PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344PZ306, 344PZ307, 344PZ308.

Table 350 Reliability Data Sensor Leg 1-3 344PZ306, 344PZ307, 344PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function is quantified as follows.

Table 351 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 352 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 353 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2) Safety Instrumented Function is quantified as follows.

Table 354 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.84E-03 | 3 | N/A | 566.9 | 1 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: NG till brännare PGH PT12

The information and reliability data underneath describe the NG till brännare PGH PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 355 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 356 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 357 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 358 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-032 SIL2 Flamvakt (344YS314|SG1)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Flamvakt (344YS314¦SG1) |
| --- | --- |
| SIF Tag | SIF-032 |
| SIF Description: | SIL2 Flamvakt (344YS314¦SG1) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 241 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 359 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.15E-03 | 241 | 2 | 2 | N/A | 21.6 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function is quantified as follows.

Table 360 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.03E-04 | 2 | N/A | ∞ | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Flamvakt

The information and reliability data underneath describe the Flamvakt sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Flamvakt |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344YS314 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344YS314

The following table shows the equipment that defines sensor leg 1-1 344YS314.

Table 361 Sensor Leg 1-1: 344YS314 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| DURAG D-LX 100UA-C1 |  | - | - | B | 3 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344YS314.

Table 362 Reliability Data Sensor Leg 1-1 344YS314

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| DURAG D-LX 100UA-C1 | - - | - - | - - | - - | - - | 1.83E-06 1.83E-06 | 4.32E-08 4.32E-08 | - - | - - | - - |
|  |  |  |  |  |  |  | SFF [%] |  |  | 97.7 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function is quantified as follows.

Table 363 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.24E-06 | 2 | N/A | 22.45 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 364 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 365 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-032 SIL2 Flamvakt (344YS314|SG1) Safety Instrumented Function is quantified as follows.

Table 366 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.84E-03 | 3 | N/A | 566.9 | 1 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 367 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 368 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: NG till brännare PGH PT12

The information and reliability data underneath describe the NG till brännare PGH PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 369 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 370 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦H2) |
| --- | --- |
| SIF Tag | SIF-033 |
| SIF Description: | SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦H2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Trip of P4 värmare (344HE002) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 459.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 371 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.17E-03 | 459.7 | 2 | 2 | N/A | 18.29 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function is quantified as follows.

Table 372 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.32E-04 | 3 | N/A | 1775.15 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp transferline efter O2-inj

The information and reliability data underneath describe the Gastemp transferline efter O2-inj sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp transferline efter O2-inj |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TZ322, 344TZ323, 344TZ324 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 344TZ322, 344TZ323, 344TZ324

The following table shows the equipment that defines sensor leg 1-3 344TZ322, 344TZ323, 344TZ324.

Table 373 Sensor Leg 1-3: 344TZ322, 344TZ323, 344TZ324 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ322, 344TZ323, 344TZ324.

Table 374 Reliability Data Sensor Leg 1-3 344TZ322, 344TZ323, 344TZ324

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function is quantified as follows.

Table 375 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 376 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 377 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2) Safety Instrumented Function is quantified as follows.

Table 378 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 379 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 380 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦L2) |
| --- | --- |
| SIF Tag | SIF-034 |
| SIF Description: | Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 3 with RRF ≥ 1000 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 3 with RRF = 1151.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 381 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.68E-04 | 1151.6 | 3 | 3 | N/A | 114.14 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function is quantified as follows.

Table 382 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.41E-06 | 3 | N/A | 3591.6 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp transferline efter O2-inj

The information and reliability data underneath describe the Gastemp transferline efter O2-inj sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp transferline efter O2-inj |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TZ322, 344TZ323, 344TZ324 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 6 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 1.5 |

##### Sensor Leg 1-3: 344TZ322, 344TZ323, 344TZ324

The following table shows the equipment that defines sensor leg 1-3 344TZ322, 344TZ323, 344TZ324.

Table 383 Sensor Leg 1-3: 344TZ322, 344TZ323, 344TZ324 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL3 [AnalogIn] | 2013.1.02 | - | - | B | 3 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 344TZ322, 344TZ323, 344TZ324.

Table 384 Reliability Data Sensor Leg 1-3 344TZ322, 344TZ323, 344TZ324

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - 4.07E-07 | - - | - 1.70E-08 | 2.70E-08 2.70E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL3 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function is quantified as follows.

Table 385 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.76E-08 | 3 | N/A | 140.5 | 1 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL3 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL3 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 1 |
| -factor [%]: | 1 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 386 ABB AC800M High Integrity SIL3 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL3 | 2013.1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL3.

Table 387 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL3

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/TP830 SM811/TP868 (SM810/P855) | 4.51E-07 | 7.54E-07 | 1.46E-06 | 5.56E-11 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: 1*SD821 + 1*SS823 + 2*MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2) Safety Instrumented Function is quantified as follows.

Table 388 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.62E-04 | 3 | N/A | 732.5 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning-O2

The information and reliability data underneath describe the Avstängning-O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning-O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 389 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 2013.1.02 | - | - | B | 3 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 390 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV¦H2/L2) |
| --- | --- |
| SIF Tag | SIF-035 |
| SIF Description: | SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV¦H2/L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 151.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 391 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.58E-03 | 151.9 | 2 | 2 | N/A | 31.96 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function is quantified as follows.

Table 392 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.53E-03 | 2 | N/A | 745306.04 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: 341XI321

The information and reliability data underneath describe the 341XI321 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 341XI321 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251PD554, 251TI554, 251PZ312, 251PZ313 |
| Voting within group: | 2oo4 |
| Voting type: | Diverse |
| HFT: | 2 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95.9 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1: 251PD554

The following table shows the equipment that defines sensor leg 1 251PD554.

Table 393 Sensor Leg 1: 251PD554 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 251PD554.

Table 394 Reliability Data Sensor Leg 1 251PD554

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.89E-08 5.17E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 5.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 251TI554

The following table shows the equipment that defines sensor leg 2 251TI554.

Table 395 Sensor Leg 2: 251TI554 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 251TI554.

Table 396 Reliability Data Sensor Leg 2 251TI554

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - - | - - | 1.07E-07 3.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 7.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 3: 251PZ312

The following table shows the equipment that defines sensor leg 3 251PZ312.

Table 397 Sensor Leg 3: 251PZ312 Details

| Sensor Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 3 251PZ312.

Table 398 Reliability Data Sensor Leg 3 251PZ312

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.53E-08 5.13E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 6.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 4: 251PZ313

The following table shows the equipment that defines sensor leg 4 251PZ313.

Table 399 Sensor Leg 4: 251PZ313 Details

| Sensor Leg 4 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 4 251PZ313.

Table 400 Reliability Data Sensor Leg 4 251PZ313

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.53E-08 5.13E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 6.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: 251XI554

The information and reliability data underneath describe the 251XI554 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 251XI554 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251TI554, 251PZ320, 344PZ321 |
| Voting within group: | 3oo3 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 94.9 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1: 251TI554

The following table shows the equipment that defines sensor leg 1 251TI554.

Table 401 Sensor Leg 1: 251TI554 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 251TI554.

Table 402 Reliability Data Sensor Leg 1 251TI554

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - - | - - | 1.07E-07 3.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 7.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 251PZ320

The following table shows the equipment that defines sensor leg 2 251PZ320.

Table 403 Sensor Leg 2: 251PZ320 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 251PZ320.

Table 404 Reliability Data Sensor Leg 2 251PZ320

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.53E-08 5.13E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 6.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 3: 344PZ321

The following table shows the equipment that defines sensor leg 3 344PZ321.

Table 405 Sensor Leg 3: 344PZ321 Details

| Sensor Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 3 344PZ321.

Table 406 Reliability Data Sensor Leg 3 344PZ321

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.53E-08 5.13E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 6.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function is quantified as follows.

Table 407 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.87E-06 | 2 | N/A | 33.4 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 408 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 409 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2) Safety Instrumented Function is quantified as follows.

Table 410 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.06E-03 | 3 | N/A | 738.1 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 411 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 412 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364¦L2) |
| --- | --- |
| SIF Tag | SIF-036 |
| SIF Description: | SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 115.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 413 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.63E-03 | 115.8 | 2 | 2 | N/A | 18.95 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function is quantified as follows.

Table 414 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.17E-04 | 3 | N/A | 10354.69 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck N2

The information and reliability data underneath describe the Gastryck N2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck N2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ362, 253PZ363, 253PZ364 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364

The following table shows the equipment that defines sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 415 Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 416 Reliability Data Sensor Leg 1-3 253PZ362, 253PZ363, 253PZ364

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function is quantified as follows.

Table 417 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 418 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 419 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2) Safety Instrumented Function is quantified as follows.

Table 420 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.21E-03 | 2 | N/A | 842.93 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 421 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 422 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close 253SV652 (SIL2) (F.O)

The information and reliability data underneath describe the Close 253SV652 (SIL2) (F.O) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 253SV652 (SIL2) (F.O) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 253SV652 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 253SV652

The following table shows the equipment that defines final element leg 1-1 253SV652.

Table 423 Final Element Leg 1-1: 253SV652 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 253SV652.

Table 424 Reliability Data Final Element Leg 1-1 253SV652

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325¦L2) |
| --- | --- |
| SIF Tag | SIF-037 |
| SIF Description: | SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325¦L2) => Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Close avstängningsventil N2 till reaktortopp (253SV607 SIL2) Close N2 till reduktionskrets (254SV582 SIL2) Close N2 till kylkrets (254SV594 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 112.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 3 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 425 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.88E-03 | 112.5 | 2 | 2 | N/A | 36.75 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function is quantified as follows.

Table 426 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.76E-05 | 3 | N/A | 3622.1 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryckvakt efter N2 bufferttank 253TA005

The information and reliability data underneath describe the Tryckvakt efter N2 bufferttank 253TA005 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt efter N2 bufferttank 253TA005 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ323, 253PZ324, 253PZ325 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 253PZ323, 253PZ324, 253PZ325

The following table shows the equipment that defines sensor leg 1-3 253PZ323, 253PZ324, 253PZ325.

Table 427 Sensor Leg 1-3: 253PZ323, 253PZ324, 253PZ325 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 253PZ323, 253PZ324, 253PZ325.

Table 428 Reliability Data Sensor Leg 1-3 253PZ323, 253PZ324, 253PZ325

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function is quantified as follows.

Table 429 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.76E-06 | 2 | N/A | 37.72 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 430 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 431 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2) Safety Instrumented Function is quantified as follows.

Table 432 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.82E-03 | 2 | N/A | 2390.36 | 0 | 3 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: | 10 |

#### Final Element Group 1: Close N2 till kylkrets

The information and reliability data underneath describe the Close N2 till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close N2 till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV594 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 254SV594

The following table shows the equipment that defines final element leg 1-1 254SV594.

Table 433 Final Element Leg 1-1: 254SV594 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV594.

Table 434 Reliability Data Final Element Leg 1-1 254SV594

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängning O2

The information and reliability data underneath describe the Avstängning O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Beta Estimator Selections

The following selections were made as part of the beta estimator for the Avstängning O2 final element group.

| Separation/Segregation |  |
| --- | --- |
| Description | Yes/No |
| Are all signal cables for the channels routed separately at all positions? | No |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel on separate printed-circuit boards? | Yes |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel indoors and in separate cabinets? | No |
| Diversity/Redundancy |  |
| Description | Yes/No |
| Do the devices employ different physical principles for the sensing elements for example, pressure and temperature, vane anemometer and Doppler transducer, etc? | No |
| Do the devices employ different electrical principles/designs for example, digital and analogue, different manufacturer (not re-badged) or different technology? | No |
| Are separate test methods and people used for each channel during commissioning? | No |
| Is maintenance on each channel carried out by different people at different times? | No |
| Complexity/Design/Application/Maturity/Experience |  |
| Description | Yes/No |
| Does cross-connection between channels preclude the exchange of any information other than that used for diagnostic testing or voting purposes? | Yes |
| Is the design based on techniques used in equipment that has been used successfully in the field for > 5 years? | Yes |
| Is there more than 5 years experience with the same hardware used in similar environments? | Yes |
| Are inputs and outputs protected from potential levels of over-voltage and over-current? | Yes |
| Are all devices/components conservatively rated (for example, by a factor of 2 or more)? | No |
| Assessment/Analysis and Feedback of Data |  |
| Description | Yes/No |
| Have the results of the failure modes and effects analysis or fault-tree analysis been examined to establish sources of common cause failure and have predetermined sources of common cause failure been eliminated by design? | Yes |
| Were common cause failures considered in design reviews with the results fed back into the design? (Documentary evidence of the design review activity is required.) | No |
| Are all field failures fully analyzed with feedback into the design? (Documentary evidence of the procedure is required.) | No |
| Procedures/Human Interface |  |
| Description | Yes/No |
| Is there a written system of work to ensure that all component failures (or degradations) are detected, the root causes established and other similar items inspected for similar potential causes of failure? | Yes |
| Are procedures in place to ensure that: maintenance (including adjustment or calibration) of any part of the independent channels is staggered, and, in addition to the manual checks carried out following maintenance, the diagnostic tests are allowed to run satisfactorily between the completion of maintenance on one channel and the start of maintenance on another? | Yes |
| Do the documented maintenance procedures specify that all parts of redundant systems (for example, cables, etc.) intended to be independent of each other, are not to be relocated? | No |
| Is all maintenance of printed-circuit boards, etc. carried out off-site at a qualified repair centre and have all the repaired items gone through a full pre-installation testing? | Yes |
| Do the system diagnostic tests report failures to the level of a field-replaceable module? | Yes |
| Competence/Training/Safety Culture |  |
| Description | Yes/No |
| Have designers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Have maintainers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Environmental Control |  |
| Description | Yes/No |
| Is personnel access limited (for example locked cabinets, inaccessible position)? | No |
| Is the system likely to operate always within the range of temperature, humidity, corrosion, dust, vibration, etc., over which it has been tested, without the use of external environmental control? | Yes |
| Are all signal and power cables separate at all positions? | No |
| Environmental Testing |  |
| Description | Yes/No |
| Has the system been tested for immunity to all relevant environmental influences (for example EMC, temperature, vibration, shock, humidity) to an appropriate level as specified in recognized standards? | No |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 435 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 436 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Close N2 Reaktor

The information and reliability data underneath describe the Close N2 Reaktor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close N2 Reaktor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 253SV607 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 253SV607

The following table shows the equipment that defines final element leg 1-1 253SV607.

Table 437 Final Element Leg 1-1: 253SV607 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 253SV607.

Table 438 Reliability Data Final Element Leg 1-1 253SV607

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 4: Close N2 mixer reaktor

The information and reliability data underneath describe the Close N2 mixer reaktor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close N2 mixer reaktor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV582 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 254SV582

The following table shows the equipment that defines final element leg 1-1 254SV582.

Table 439 Final Element Leg 1-1: 254SV582 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV582.

Table 440 Reliability Data Final Element Leg 1-1 254SV582

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) |
| --- | --- |
| SIF Tag | SIF-038 |
| SIF Description: | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) => Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 395.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: | IEC 61511 - Functional safety: Safety Instrumented Systems for the Process Industry Sector |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 441 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.53E-03 | 395.8 | 2 | 2 | N/A | 17.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 442 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.05E-04 | 3 | N/A | 228.67 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög vätskenivå WESP

The information and reliability data underneath describe the Hög vätskenivå WESP sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög vätskenivå WESP |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345LI354, 345LI355, 345LI356 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 345LI354, 345LI355, 345LI356

The following table shows the equipment that defines sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 443 Sensor Leg 1-3: 345LI354, 345LI355, 345LI356 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Enderess Hauser FMR50-57 |  | - | - | B | 3 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 444 Reliability Data Sensor Leg 1-3 345LI354, 345LI355, 345LI356

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Enderess Hauser FMR50-57 | - - | - - | - - | - - | 2.33E-06 2.33E-06 | - - | 2.49E-07 2.49E-07 | - - | - - | - - |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 445 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 446 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 447 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 448 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.12E-03 | 2 | N/A | 1095.15 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 449 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 450 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 451 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 452 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryck efter WESP red. gaskrets (345PI361¦H2) |
| --- | --- |
| SIF Tag | SIF-039 |
| SIF Description: | SIL2 Tryck efter WESP red. gaskrets (345PI361¦H2) => Open Avstängningsventiler venturi reduktionsgas (345SV520/21/22 SIL2) Open Topptryck nödventil eft. våtelfilter red. gas (345SV599 ) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 187.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 453 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.32E-03 | 187.9 | 2 | 2 | N/A | 17.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function is quantified as follows.

Table 454 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.89E-04 | 2 | N/A | 273.24 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: SIL2 Tryck efter WESP red. gaskrets

The information and reliability data underneath describe the SIL2 Tryck efter WESP red. gaskrets sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIL2 Tryck efter WESP red. gaskrets |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345PI361 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 345PI361

The following table shows the equipment that defines sensor leg 1-1 345PI361.

Table 455 Sensor Leg 1-1: 345PI361 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345PI361.

Table 456 Reliability Data Sensor Leg 1-1 345PI361

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function is quantified as follows.

Table 457 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 458 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 459 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2) Safety Instrumented Function is quantified as follows.

Table 460 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.63E-03 | 2 | N/A | 750.88 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Open Avstängningsventiler venturi reduktionsgas

The information and reliability data underneath describe the Open Avstängningsventiler venturi reduktionsgas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open Avstängningsventiler venturi reduktionsgas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV520, 345SV521, 345SV522 |
| Voting within group: | 1oo3 |
| Voting type: | Diverse |
| HFT: | 2 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 345SV520

The following table shows the equipment that defines final element leg 1 345SV520.

Table 461 Final Element Leg 1: 345SV520 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 345SV520.

Table 462 Reliability Data Final Element Leg 1 345SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 345SV521

The following table shows the equipment that defines final element leg 2 345SV521.

Table 463 Final Element Leg 2: 345SV521 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 345SV521.

Table 464 Reliability Data Final Element Leg 2 345SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 3: 345SV522

The following table shows the equipment that defines final element leg 3 345SV522.

Table 465 Final Element Leg 3: 345SV522 Details

| Final ELement Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 3 345SV522.

Table 466 Reliability Data Final Element Leg 3 345SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | 1.46E-07 | - | 3.22E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 24.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Open Topptryck nödventil eft. våtelfilter red. gas

The information and reliability data underneath describe the Open Topptryck nödventil eft. våtelfilter red. gas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open Topptryck nödventil eft. våtelfilter red. gas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV599 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 96.5 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 73.3 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 345SV599

The following table shows the equipment that defines final element leg 1-1 345SV599.

Table 467 Final Element Leg 1-1: 345SV599 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV599.

Table 468 Reliability Data Final Element Leg 1-1 345SV599

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - - | - - | - 2.47E-07 | 3.70E-07 1.23E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 13.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryck efter WESP processgaskrets (353PI361¦H2) |
| --- | --- |
| SIF Tag | SIF-040 |
| SIF Description: | SIL2 Tryck efter WESP processgaskrets (353PI361¦H2) => Open Avstängningsventiler venturi processgas (353SV520/21/22 SIL2) Open Topptryck nödventil eft. våtelfilter red. gas (353SV599 ) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 187.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 469 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.32E-03 | 187.9 | 2 | 2 | N/A | 17.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function is quantified as follows.

Table 470 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.89E-04 | 2 | N/A | 273.24 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck efter WESP processgaskrets

The information and reliability data underneath describe the Tryck efter WESP processgaskrets sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck efter WESP processgaskrets |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353PI361 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353PI361

The following table shows the equipment that defines sensor leg 1-1 353PI361.

Table 471 Sensor Leg 1-1: 353PI361 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353PI361.

Table 472 Reliability Data Sensor Leg 1-1 353PI361

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function is quantified as follows.

Table 473 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 474 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 475 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2) Safety Instrumented Function is quantified as follows.

Table 476 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.63E-03 | 2 | N/A | 750.88 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängningsventiler venturi processgas

The information and reliability data underneath describe the Avstängningsventiler venturi processgas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventiler venturi processgas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV520, 353SV521, 353SV522 |
| Voting within group: | 1oo3 |
| Voting type: | Diverse |
| HFT: | 2 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 353SV520

The following table shows the equipment that defines final element leg 1 353SV520.

Table 477 Final Element Leg 1: 353SV520 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 353SV520.

Table 478 Reliability Data Final Element Leg 1 353SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 353SV521

The following table shows the equipment that defines final element leg 2 353SV521.

Table 479 Final Element Leg 2: 353SV521 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 353SV521.

Table 480 Reliability Data Final Element Leg 2 353SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 3: 353SV522

The following table shows the equipment that defines final element leg 3 353SV522.

Table 481 Final Element Leg 3: 353SV522 Details

| Final ELement Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 3 353SV522.

Table 482 Reliability Data Final Element Leg 3 353SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | 1.46E-07 | - | 3.22E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 24.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Topptryck nödventil eft. våtelfilter red. gas

The information and reliability data underneath describe the Topptryck nödventil eft. våtelfilter red. gas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Topptryck nödventil eft. våtelfilter red. gas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV599 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 96.5 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 73.3 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 353SV599

The following table shows the equipment that defines final element leg 1-1 353SV599.

Table 483 Final Element Leg 1-1: 353SV599 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353SV599.

Table 484 Reliability Data Final Element Leg 1-1 353SV599

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - - | - - | - 2.47E-07 | 3.70E-07 1.23E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 13.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temp kondensor reduktionsgas (345TI301¦H2) |
| --- | --- |
| SIF Tag | SIF-041 |
| SIF Description: | SIL1 Temp kondensor reduktionsgas (345TI301¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 86.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 485 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.15E-02 | 86.6 | 1 | 2 | N/A | 16.24 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function is quantified as follows.

Table 486 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-03 | 2 | N/A | 554.98 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp kondensor reduktionsgas

The information and reliability data underneath describe the Temp kondensor reduktionsgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp kondensor reduktionsgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345TI301 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 345TI301

The following table shows the equipment that defines sensor leg 1-1 345TI301.

Table 487 Sensor Leg 1-1: 345TI301 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345TI301.

Table 488 Reliability Data Sensor Leg 1-1 345TI301

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function is quantified as follows.

Table 489 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.49E-06 | 2 | N/A | 16.94 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 490 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 491 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2) Safety Instrumented Function is quantified as follows.

Table 492 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.02E-02 | 2 | N/A | 1344.25 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 493 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 494 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 495 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 496 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 SIL2 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101 SIL2

The following table shows the equipment that defines final element leg 1-1 346PU101 SIL2.

Table 497 Final Element Leg 1-1: 346PU101 SIL2 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101 SIL2.

Table 498 Reliability Data Final Element Leg 1-1 346PU101 SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-042 SIL1 Temp kondensor processgas (353TI301|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Temp kondensor processgas (353TI301¦H2) |
| --- | --- |
| SIF Tag | SIF-042 |
| SIF Description: | SIL1 Temp kondensor processgas (353TI301¦H2) => Trip Processgaskompressor (354PU101 SIL2) Close NG till kylkrets (252SV614 SIL2) Close H2 till uppkolningskrets (341SV881) Close CO till uppkolningskrets (356SV511) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 199.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 499 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.00E-03 | 199.8 | 2 | 2 | N/A | 16.23 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function is quantified as follows.

Table 500 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-03 | 2 | N/A | 554.98 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp kondensor processgas

The information and reliability data underneath describe the Temp kondensor processgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp kondensor processgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353TI301 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353TI301

The following table shows the equipment that defines sensor leg 1-1 353TI301.

Table 501 Sensor Leg 1-1: 353TI301 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353TI301.

Table 502 Reliability Data Sensor Leg 1-1 353TI301

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function is quantified as follows.

Table 503 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.49E-06 | 2 | N/A | 16.94 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 504 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 505 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-042 SIL1 Temp kondensor processgas (353TI301|H2) Safety Instrumented Function is quantified as follows.

Table 506 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.60E-03 | 2 | N/A | 1286.95 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 507 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 508 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close NG till kylkrets

The information and reliability data underneath describe the Close NG till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close NG till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV614 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 77 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 252SV614

The following table shows the equipment that defines final element leg 1-1 252SV614.

Table 509 Final Element Leg 1-1: 252SV614 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 252SV614.

Table 510 Reliability Data Final Element Leg 1-1 252SV614

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Transworld Mars | - - | - - | - - | 3.73E-07 - | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Skintemp förquench reduktionsgas (345TI307¦H2) |
| --- | --- |
| SIF Tag | SIF-043 |
| SIF Description: | SIL2 Skintemp förquench reduktionsgas (345TI307¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 168.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 511 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.94E-03 | 168.3 | 2 | 2 | N/A | 28.2 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function is quantified as follows.

Table 512 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.20E-04 | 2 | N/A | 1082.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Skintemp förquench reduktionsgas

The information and reliability data underneath describe the Skintemp förquench reduktionsgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Skintemp förquench reduktionsgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345TI307 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 345TI307

The following table shows the equipment that defines sensor leg 1-1 345TI307.

Table 513 Sensor Leg 1-1: 345TI307 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345TI307.

Table 514 Reliability Data Sensor Leg 1-1 345TI307

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function is quantified as follows.

Table 515 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.05E-06 | 2 | N/A | 29.3 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 516 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 517 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2) Safety Instrumented Function is quantified as follows.

Table 518 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.22E-03 | 2 | N/A | 2498.19 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH PT 6

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH PT 6 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH PT 6 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 519 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 520 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängning O2

The information and reliability data underneath describe the Avstängning O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Beta Estimator Selections

The following selections were made as part of the beta estimator for the Avstängning O2 final element group.

| Separation/Segregation |  |
| --- | --- |
| Description | Yes/No |
| Are all signal cables for the channels routed separately at all positions? | No |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel on separate printed-circuit boards? | Yes |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel indoors and in separate cabinets? | No |
| Diversity/Redundancy |  |
| Description | Yes/No |
| Do the devices employ different physical principles for the sensing elements for example, pressure and temperature, vane anemometer and Doppler transducer, etc? | No |
| Do the devices employ different electrical principles/designs for example, digital and analogue, different manufacturer (not re-badged) or different technology? | No |
| Are separate test methods and people used for each channel during commissioning? | No |
| Is maintenance on each channel carried out by different people at different times? | No |
| Complexity/Design/Application/Maturity/Experience |  |
| Description | Yes/No |
| Does cross-connection between channels preclude the exchange of any information other than that used for diagnostic testing or voting purposes? | Yes |
| Is the design based on techniques used in equipment that has been used successfully in the field for > 5 years? | Yes |
| Is there more than 5 years experience with the same hardware used in similar environments? | Yes |
| Are inputs and outputs protected from potential levels of over-voltage and over-current? | Yes |
| Are all devices/components conservatively rated (for example, by a factor of 2 or more)? | No |
| Assessment/Analysis and Feedback of Data |  |
| Description | Yes/No |
| Have the results of the failure modes and effects analysis or fault-tree analysis been examined to establish sources of common cause failure and have predetermined sources of common cause failure been eliminated by design? | Yes |
| Were common cause failures considered in design reviews with the results fed back into the design? (Documentary evidence of the design review activity is required.) | No |
| Are all field failures fully analyzed with feedback into the design? (Documentary evidence of the procedure is required.) | No |
| Procedures/Human Interface |  |
| Description | Yes/No |
| Is there a written system of work to ensure that all component failures (or degradations) are detected, the root causes established and other similar items inspected for similar potential causes of failure? | Yes |
| Are procedures in place to ensure that: maintenance (including adjustment or calibration) of any part of the independent channels is staggered, and, in addition to the manual checks carried out following maintenance, the diagnostic tests are allowed to run satisfactorily between the completion of maintenance on one channel and the start of maintenance on another? | Yes |
| Do the documented maintenance procedures specify that all parts of redundant systems (for example, cables, etc.) intended to be independent of each other, are not to be relocated? | No |
| Is all maintenance of printed-circuit boards, etc. carried out off-site at a qualified repair centre and have all the repaired items gone through a full pre-installation testing? | Yes |
| Do the system diagnostic tests report failures to the level of a field-replaceable module? | Yes |
| Competence/Training/Safety Culture |  |
| Description | Yes/No |
| Have designers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Have maintainers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Environmental Control |  |
| Description | Yes/No |
| Is personnel access limited (for example locked cabinets, inaccessible position)? | No |
| Is the system likely to operate always within the range of temperature, humidity, corrosion, dust, vibration, etc., over which it has been tested, without the use of external environmental control? | Yes |
| Are all signal and power cables separate at all positions? | No |
| Environmental Testing |  |
| Description | Yes/No |
| Has the system been tested for immunity to all relevant environmental influences (for example EMC, temperature, vibration, shock, humidity) to an appropriate level as specified in recognized standards? | No |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 521 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 522 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 523 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 524 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Skintemp quench reduktionsgas (345TI308¦H2) |
| --- | --- |
| SIF Tag | SIF-044 |
| SIF Description: | SIL2 Skintemp förquench reduktionsgas (345TI307¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 168.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 525 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.94E-03 | 168.3 | 2 | 2 | N/A | 28.2 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function is quantified as follows.

Table 526 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.20E-04 | 2 | N/A | 1082.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Skintemp quench reduktionsgas

The information and reliability data underneath describe the Skintemp quench reduktionsgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Skintemp quench reduktionsgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345TI308 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 345TI308

The following table shows the equipment that defines sensor leg 1-1 345TI308.

Table 527 Sensor Leg 1-1: 345TI308 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345TI308.

Table 528 Reliability Data Sensor Leg 1-1 345TI308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function is quantified as follows.

Table 529 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.05E-06 | 2 | N/A | 29.3 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 530 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 531 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2) Safety Instrumented Function is quantified as follows.

Table 532 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.22E-03 | 2 | N/A | 2498.19 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH PT 6

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH PT 6 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH PT 6 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 533 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 534 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängning O2

The information and reliability data underneath describe the Avstängning O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Beta Estimator Selections

The following selections were made as part of the beta estimator for the Avstängning O2 final element group.

| Separation/Segregation |  |
| --- | --- |
| Description | Yes/No |
| Are all signal cables for the channels routed separately at all positions? | No |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel on separate printed-circuit boards? | Yes |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel indoors and in separate cabinets? | No |
| Diversity/Redundancy |  |
| Description | Yes/No |
| Do the devices employ different physical principles for the sensing elements for example, pressure and temperature, vane anemometer and Doppler transducer, etc? | No |
| Do the devices employ different electrical principles/designs for example, digital and analogue, different manufacturer (not re-badged) or different technology? | No |
| Are separate test methods and people used for each channel during commissioning? | No |
| Is maintenance on each channel carried out by different people at different times? | No |
| Complexity/Design/Application/Maturity/Experience |  |
| Description | Yes/No |
| Does cross-connection between channels preclude the exchange of any information other than that used for diagnostic testing or voting purposes? | Yes |
| Is the design based on techniques used in equipment that has been used successfully in the field for > 5 years? | Yes |
| Is there more than 5 years experience with the same hardware used in similar environments? | Yes |
| Are inputs and outputs protected from potential levels of over-voltage and over-current? | Yes |
| Are all devices/components conservatively rated (for example, by a factor of 2 or more)? | No |
| Assessment/Analysis and Feedback of Data |  |
| Description | Yes/No |
| Have the results of the failure modes and effects analysis or fault-tree analysis been examined to establish sources of common cause failure and have predetermined sources of common cause failure been eliminated by design? | Yes |
| Were common cause failures considered in design reviews with the results fed back into the design? (Documentary evidence of the design review activity is required.) | No |
| Are all field failures fully analyzed with feedback into the design? (Documentary evidence of the procedure is required.) | No |
| Procedures/Human Interface |  |
| Description | Yes/No |
| Is there a written system of work to ensure that all component failures (or degradations) are detected, the root causes established and other similar items inspected for similar potential causes of failure? | Yes |
| Are procedures in place to ensure that: maintenance (including adjustment or calibration) of any part of the independent channels is staggered, and, in addition to the manual checks carried out following maintenance, the diagnostic tests are allowed to run satisfactorily between the completion of maintenance on one channel and the start of maintenance on another? | Yes |
| Do the documented maintenance procedures specify that all parts of redundant systems (for example, cables, etc.) intended to be independent of each other, are not to be relocated? | No |
| Is all maintenance of printed-circuit boards, etc. carried out off-site at a qualified repair centre and have all the repaired items gone through a full pre-installation testing? | Yes |
| Do the system diagnostic tests report failures to the level of a field-replaceable module? | Yes |
| Competence/Training/Safety Culture |  |
| Description | Yes/No |
| Have designers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Have maintainers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Environmental Control |  |
| Description | Yes/No |
| Is personnel access limited (for example locked cabinets, inaccessible position)? | No |
| Is the system likely to operate always within the range of temperature, humidity, corrosion, dust, vibration, etc., over which it has been tested, without the use of external environmental control? | Yes |
| Are all signal and power cables separate at all positions? | No |
| Environmental Testing |  |
| Description | Yes/No |
| Has the system been tested for immunity to all relevant environmental influences (for example EMC, temperature, vibration, shock, humidity) to an appropriate level as specified in recognized standards? | No |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 535 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 536 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 537 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 538 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Skintemp förquench processgas (353TI307¦H2) |
| --- | --- |
| SIF Tag | SIF-045 |
| SIF Description: | SIL2 Skintemp förquench processgas (353TI307¦H2) => Trip Processgaskompressor (354PU101 SIL2) Close NG till kylkrets (252SV614 SIL2) Close H2 till uppkolningskrets (341SV881) Close CO till uppkolningskrets (356SV511) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 154.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 539 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.49E-03 | 154.1 | 2 | 2 | N/A | 25.47 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function is quantified as follows.

Table 540 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.20E-04 | 2 | N/A | 1082.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Skintemp förquench processgas

The information and reliability data underneath describe the Skintemp förquench processgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Skintemp förquench processgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353TI307 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 353TI307

The following table shows the equipment that defines sensor leg 1-1 353TI307.

Table 541 Sensor Leg 1-1: 353TI307 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353TI307.

Table 542 Reliability Data Sensor Leg 1-1 353TI307

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function is quantified as follows.

Table 543 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.21E-06 | 2 | N/A | 26.31 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 544 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 545 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2) Safety Instrumented Function is quantified as follows.

Table 546 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.77E-03 | 2 | N/A | 2975.01 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 547 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 548 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Close NG till kylkrets

The information and reliability data underneath describe the Close NG till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close NG till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV614 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |
| End of Batch Test Interval: | 6M |
| End of Batch Test Coverage [%]: | 77 |
| End of Batch Test Execution: | Manual |

##### Final Element Leg 1-1: 252SV614

The following table shows the equipment that defines final element leg 1-1 252SV614.

Table 549 Final Element Leg 1-1: 252SV614 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 252SV614.

Table 550 Reliability Data Final Element Leg 1-1 252SV614

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Transworld Mars | - - | - - | - - | 3.73E-07 - | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Close H2 till uppkolningskrets

The information and reliability data underneath describe the Close H2 till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close H2 till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV881 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 341SV881

The following table shows the equipment that defines final element leg 1-1 341SV881.

Table 551 Final Element Leg 1-1: 341SV881 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV881.

Table 552 Reliability Data Final Element Leg 1-1 341SV881

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 4: Close CO till uppkolningskrets

The information and reliability data underneath describe the Close CO till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close CO till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV511 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 356SV511

The following table shows the equipment that defines final element leg 1-1 356SV511.

Table 553 Final Element Leg 1-1: 356SV511 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 356SV511.

Table 554 Reliability Data Final Element Leg 1-1 356SV511

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-046 SIL2 Skintemp quench processgas (353TI308|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Skintemp quench processgas (353TI308¦H2) |
| --- | --- |
| SIF Tag | SIF-046 |
| SIF Description: | SIL2 Skintemp quench processgas (353TI308¦H2) => Trip Processgaskompressor (354PU101 SIL2) Close NG till kylkrets (252SV614/252RV618 SIL2) Close H2 till uppkolningskrets (341SV881) Close CO till uppkolningskrets (356SV511) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 199 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 555 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.02E-03 | 199 | 2 | 2 | N/A | 20.6 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function is quantified as follows.

Table 556 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-03 | 2 | N/A | 119.15 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Skintemp quench processgas

The information and reliability data underneath describe the Skintemp quench processgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Skintemp quench processgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353TI308 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353TI308

The following table shows the equipment that defines sensor leg 1-1 353TI308.

Table 557 Sensor Leg 1-1: 353TI308 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353TI308.

Table 558 Reliability Data Sensor Leg 1-1 353TI308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 89.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function is quantified as follows.

Table 559 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 560 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 561 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-046 SIL2 Skintemp quench processgas (353TI308|H2) Safety Instrumented Function is quantified as follows.

Table 562 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.63E-03 | 2 | N/A | 314.84 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 563 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 564 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close NG till kylkrets

The information and reliability data underneath describe the Close NG till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close NG till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV614 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 77 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 252SV614

The following table shows the equipment that defines final element leg 1-1 252SV614.

Table 565 Final Element Leg 1-1: 252SV614 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 252SV614.

Table 566 Reliability Data Final Element Leg 1-1 252SV614

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Transworld Mars | - - | - - | - - | 3.73E-07 - | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305¦L2) |
| --- | --- |
| SIF Tag | SIF-047 |
| SIF Description: | SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305¦L2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) Trip Reduktionsgaskompressor (346PU101 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 90.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 567 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.11E-02 | 90.3 | 1 | 2 | N/A | 12.18 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function is quantified as follows.

Table 568 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.01E-03 | 2 | N/A | 33.51 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Flödesmätare till förquench reduktionsgaskrets

The information and reliability data underneath describe the Flödesmätare till förquench reduktionsgaskrets sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Flödesmätare till förquench reduktionsgaskrets |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345FI305 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 345FI305

The following table shows the equipment that defines sensor leg 1-1 345FI305.

Table 569 Sensor Leg 1-1: 345FI305 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Promag P200 |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345FI305.

Table 570 Reliability Data Sensor Leg 1-1 345FI305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Promag P200 | - - | - - | - - | - - | 3.39E-06 3.39E-06 | - - | 1.55E-07 1.55E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function is quantified as follows.

Table 571 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 572 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 573 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2) Safety Instrumented Function is quantified as follows.

Table 574 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.01E-02 | 2 | N/A | 1280.3 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 575 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 576 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 577 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 578 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 579 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 580 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Flödesmätare till förquench processgaskrets (353FI305¦L2) |
| --- | --- |
| SIF Tag | SIF-048 |
| SIF Description: | SIL1 Flödesmätare till förquench processgaskrets (353FI305¦L2) => Trip Processgaskompressor (354PU101 SIL2) Close NG till kylkrets (252SV614 SIL2) Close H2 till uppkolningskrets (341SV881) Close CO till uppkolningskrets (356SV511) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 215.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61508 |
| Consider Systematic Capability: | Yes |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 581 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61508 | Systematic Capability |  |
| 4.63E-03 | 215.7 | 2 | 1 | 2 | 13.06 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function is quantified as follows.

Table 582 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 1.01E-03 | 2 | 2 | 27.45 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Flödesmätare till förquench processgaskrets

The information and reliability data underneath describe the Flödesmätare till förquench processgaskrets sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Flödesmätare till förquench processgaskrets |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353FI305 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353FI305

The following table shows the equipment that defines sensor leg 1-1 353FI305.

Table 583 Sensor Leg 1-1: 353FI305 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Promag P200 |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353FI305.

Table 584 Reliability Data Sensor Leg 1-1 353FI305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Promag P200 | - - | - - | - - | - - | 3.39E-06 3.39E-06 | - - | 1.55E-07 1.55E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 96.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function is quantified as follows.

Table 585 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | 2 | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 586 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | 2 |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 587 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2) Safety Instrumented Function is quantified as follows.

Table 588 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 3.63E-03 | 1 | 3 | 314.84 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 589 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 590 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close NG till kylkrets

The information and reliability data underneath describe the Close NG till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close NG till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV614 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 77 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 252SV614

The following table shows the equipment that defines final element leg 1-1 252SV614.

Table 591 Final Element Leg 1-1: 252SV614 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 252SV614.

Table 592 Reliability Data Final Element Leg 1-1 252SV614

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Transworld Mars | - - | - - | - - | 3.73E-07 - | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-049 |
| SIF Description: | SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 445.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 593 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.24E-03 | 445.7 | 2 | 2 | N/A | 17.74 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 594 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.08E-03 | 2 | N/A | 257.02 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög Nivå kondesseparator inlopp red.gaskompressor

The information and reliability data underneath describe the Hög Nivå kondesseparator inlopp red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög Nivå kondesseparator inlopp red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 346LI300 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 346LI300

The following table shows the equipment that defines sensor leg 1-1 346LI300.

Table 595 Sensor Leg 1-1: 346LI300 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 346LI300.

Table 596 Reliability Data Sensor Leg 1-1 346LI300

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 59.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 597 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 598 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 599 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 600 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 SIL2 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101 SIL2

The following table shows the equipment that defines final element leg 1-1 346PU101 SIL2.

Table 601 Final Element Leg 1-1: 346PU101 SIL2 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101 SIL2.

Table 602 Reliability Data Final Element Leg 1-1 346PU101 SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck inlopp red.gaskompressor (346PI304¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-050 |
| SIF Description: | SIL2 Gastryck inlopp red.gaskompressor (346PI304¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 736.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 603 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.36E-03 | 736.8 | 2 | 2 | N/A | 17.54 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 604 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.27E-03 | 2 | N/A | 220.37 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck inlopp red.gaskompressor

The information and reliability data underneath describe the Gastryck inlopp red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck inlopp red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 346PI304 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 346PI304

The following table shows the equipment that defines sensor leg 1-1 346PI304.

Table 605 Sensor Leg 1-1: 346PI304 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 346PI304.

Table 606 Reliability Data Sensor Leg 1-1 346PI304

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 3.50E-07 | - - | 8.00E-08 1.49E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 607 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 608 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 609 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 610 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.93E-05 | 2 | N/A | 990.65 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 611 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 612 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-051 |
| SIF Description: | SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 981.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 613 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.02E-03 | 981.2 | 2 | 2 | N/A | 17.87 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 614 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.59E-04 | 2 | N/A | 287.37 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp eft. kylare red.gaskompressor

The information and reliability data underneath describe the Gastemp eft. kylare red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp eft. kylare red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 346TI410 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 346TI410

The following table shows the equipment that defines sensor leg 1-1 346TI410.

Table 615 Sensor Leg 1-1: 346TI410 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 346TI410.

Table 616 Reliability Data Sensor Leg 1-1 346TI410

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 617 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 618 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 619 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 620 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 621 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 622 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-052 |
| SIF Description: | SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 445.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 623 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.24E-03 | 445.7 | 2 | 2 | N/A | 17.74 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 624 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.08E-03 | 2 | N/A | 257.02 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög Nivå kondensseparator utlopp red.gaskompressor

The information and reliability data underneath describe the Hög Nivå kondensseparator utlopp red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög Nivå kondensseparator utlopp red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 346LI311 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 346LI311

The following table shows the equipment that defines sensor leg 1-1 346LI311.

Table 625 Sensor Leg 1-1: 346LI311 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 346LI311.

Table 626 Reliability Data Sensor Leg 1-1 346LI311

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 59.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 627 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 628 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 629 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 630 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 631 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 632 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Lågt oljetryck red.gaskompressor (346PI334¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-053 |
| SIF Description: | SIL2 Lågt oljetryck red.gaskompressor (346PI334¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 743.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 633 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.34E-03 | 743.8 | 2 | 2 | N/A | 17.46 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 634 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.18E-03 | 2 | N/A | 208.68 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lågt oljetryck red.gaskompressor

The information and reliability data underneath describe the Lågt oljetryck red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lågt oljetryck red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 346PI334 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 346PI334

The following table shows the equipment that defines sensor leg 1-1 346PI334.

Table 635 Sensor Leg 1-1: 346PI334 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 346PI334.

Table 636 Reliability Data Sensor Leg 1-1 346PI334

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 637 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 638 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 639 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 640 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 641 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 642 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-054 |
| SIF Description: | SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 445.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 643 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.24E-03 | 445.7 | 2 | 2 | N/A | 17.74 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 644 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.08E-03 | 2 | N/A | 257.02 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög Nivå kondensseparator inlopp proc.gaskompressor

The information and reliability data underneath describe the Hög Nivå kondensseparator inlopp proc.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög Nivå kondensseparator inlopp proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354LI300 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354LI300

The following table shows the equipment that defines sensor leg 1-1 354LI300.

Table 645 Sensor Leg 1-1: 354LI300 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354LI300.

Table 646 Reliability Data Sensor Leg 1-1 354LI300

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 59.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 647 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 648 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 649 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 650 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 651 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 652 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck inlopp proc.gaskompressor (354PI304¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-055 |
| SIF Description: | SIL2 Gastryck inlopp proc.gaskompressor (354PI304¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 699 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 653 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.43E-03 | 699 | 2 | 2 | N/A | 17.54 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 654 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.27E-03 | 2 | N/A | 220.37 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastryck inlopp proc.gaskompressor

The information and reliability data underneath describe the Gastryck inlopp proc.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck inlopp proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354PI304 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354PI304

The following table shows the equipment that defines sensor leg 1-1 354PI304.

Table 655 Sensor Leg 1-1: 354PI304 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354PI304.

Table 656 Reliability Data Sensor Leg 1-1 354PI304

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 3.50E-07 | - - | 8.00E-08 1.49E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 657 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 658 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 659 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 660 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 661 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 662 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-056 |
| SIF Description: | SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 445.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 663 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.24E-03 | 445.7 | 2 | 2 | N/A | 17.74 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 664 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.08E-03 | 2 | N/A | 257.02 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög Nivå kondensseparator utlopp proc.gaskompressor

The information and reliability data underneath describe the Hög Nivå kondensseparator utlopp proc.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög Nivå kondensseparator utlopp proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354LI311 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97.5 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354LI311

The following table shows the equipment that defines sensor leg 1-1 354LI311.

Table 665 Sensor Leg 1-1: 354LI311 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354LI311.

Table 666 Reliability Data Sensor Leg 1-1 354LI311

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.89E-08 1.21E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 59.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 667 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 668 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 669 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 670 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 671 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 672 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Lågt oljetryck proc.gaskompressor (354PI354¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-057 |
| SIF Description: | SIL2 Lågt oljetryck proc.gaskompressor (354PI354¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 743.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 673 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.34E-03 | 743.8 | 2 | 2 | N/A | 17.46 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 674 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.18E-03 | 2 | N/A | 208.68 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lågt oljetryck proc.gaskompressor

The information and reliability data underneath describe the Lågt oljetryck proc.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lågt oljetryck proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354PI354 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354PI354

The following table shows the equipment that defines sensor leg 1-1 354PI354.

Table 675 Sensor Leg 1-1: 354PI354 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354PI354.

Table 676 Reliability Data Sensor Leg 1-1 354PI354

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 73.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 677 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 678 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 679 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 680 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 681 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 682 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-058 SIL1 Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Syrehalt gasväg (345AZ362¦H2) => Trip Högspänningsenhet (345EC015) |
| --- | --- |
| SIF Tag | SIF-058 |
| SIF Description: | SIL1 Syrehalt gasväg (345AZ362¦H2) => Trip Högspänningsenhet (345EC015) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 60.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 3 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 683 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.66E-02 | 60.1 | 1 | 2 | N/A | 14.4 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function is quantified as follows.

Table 684 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.30E-02 | 2 | N/A | 151.42 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Syrehalt gasväg

The information and reliability data underneath describe the Syrehalt gasväg sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Syrehalt gasväg |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345AZ362 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 72 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 345AZ362

The following table shows the equipment that defines sensor leg 1-1 345AZ362.

Table 685 Sensor Leg 1-1: 345AZ362 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Siemens Sitrans SL |  | - | - | B | 1 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345AZ362.

Table 686 Reliability Data Sensor Leg 1-1 345AZ362

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Siemens Sitrans SL | - - | - - | - - | - - | 7.41E-07 7.41E-07 | - - | 1.16E-06 1.16E-06 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 39.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function is quantified as follows.

Table 687 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 688 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 689 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015) Safety Instrumented Function is quantified as follows.

Table 690 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.64E-03 | 2 | N/A | 87.84 | 0 | 3 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Högspänningsenhet

The information and reliability data underneath describe the Trip Högspänningsenhet final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Högspänningsenhet |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345EC015 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345EC015

The following table shows the equipment that defines final element leg 1-1 345EC015.

Table 691 Final Element Leg 1-1: 345EC015 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic MCC - interrupt function 10 < HP <=100 | 2012.Q3.02 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345EC015.

Table 692 Reliability Data Final Element Leg 1-1 345EC015

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic MCC - interrupt function 10 < HP <=100 | - | 1.20E-06 | - | 7.20E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 64.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-059 SIL2 Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) |
| --- | --- |
| SIF Tag | SIF-059 |
| SIF Description: | SIL2 Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 123.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 693 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.08E-03 | 123.7 | 2 | 2 | N/A | 37.14 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function is quantified as follows.

Table 694 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.16E-04 | 2 | N/A | 20212.05 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Vätsketryck nedströms pump

The information and reliability data underneath describe the Vätsketryck nedströms pump sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätsketryck nedströms pump |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345PI326 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 345PI326

The following table shows the equipment that defines sensor leg 1-1 345PI326.

Table 695 Sensor Leg 1-1: 345PI326 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345PI326.

Table 696 Reliability Data Sensor Leg 1-1 345PI326

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 88.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Vätsketryck nedströms pump

The information and reliability data underneath describe the Vätsketryck nedströms pump sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätsketryck nedströms pump |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ321, 320PZ322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 697 Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 698 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ321, 320PZ322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function is quantified as follows.

Table 699 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.79E-06 | 2 | N/A | 37.91 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 700 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 701 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) Safety Instrumented Function is quantified as follows.

Table 702 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.67E-03 | 2 | N/A | 2031.38 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 5 |

#### Final Element Group 1: Close Avblödning slamvatten

The information and reliability data underneath describe the Close Avblödning slamvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avblödning slamvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV566 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 345SV566

The following table shows the equipment that defines final element leg 1-1 345SV566.

Table 703 Final Element Leg 1-1: 345SV566 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV566.

Table 704 Reliability Data Final Element Leg 1-1 345SV566

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Close Från Cyklon

The information and reliability data underneath describe the Close Från Cyklon final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Från Cyklon |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV651 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 345SV651

The following table shows the equipment that defines final element leg 1-1 345SV651.

Table 705 Final Element Leg 1-1: 345SV651 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV651.

Table 706 Reliability Data Final Element Leg 1-1 345SV651

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-060 SIL2 Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätskenivå sludge tank (345LS310¦H2) => Close Avstängning tillopp spolvatten (345SV634) |
| --- | --- |
| SIF Tag | SIF-060 |
| SIF Description: | SIL2 Vätskenivå sludge tank (345LS310¦H2) => Close Avstängning tillopp spolvatten (345SV634) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 126.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 707 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.90E-03 | 126.5 | 2 | 2 | N/A | 18.31 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 708 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.69E-04 | 2 | N/A | 576.96 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Vätskenivå sludge tank

The information and reliability data underneath describe the Vätskenivå sludge tank sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätskenivå sludge tank |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345LS310 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 345LS310

The following table shows the equipment that defines sensor leg 1-1 345LS310.

Table 709 Sensor Leg 1-1: 345LS310 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345LS310.

Table 710 Reliability Data Sensor Leg 1-1 345LS310

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 77.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 711 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 712 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 713 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 714 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.23E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV634 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV634

The following table shows the equipment that defines final element leg 1-1 345SV634.

Table 715 Final Element Leg 1-1: 345SV634 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV634.

Table 716 Reliability Data Final Element Leg 1-1 345SV634

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-061 SIL2 Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 )

This chapter details the SIL Verification results, selections, and assumptions for the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätskenivå sludge tank (345LS312¦L2) => Close Avblödning slamvatten (345SV566 ) |
| --- | --- |
| SIF Tag | SIF-061 |
| SIF Description: | SIL2 Vätskenivå sludge tank (345LS312¦L2) => Close Avblödning slamvatten (345SV566 ) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 123.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 717 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.09E-03 | 123.6 | 2 | 2 | N/A | 31.67 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function is quantified as follows.

Table 718 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.23E-04 | 2 | N/A | 1212.32 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Vätskenivå sludge tank

The information and reliability data underneath describe the Vätskenivå sludge tank sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätskenivå sludge tank |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345LS312 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 345LS312

The following table shows the equipment that defines sensor leg 1-1 345LS312.

Table 719 Sensor Leg 1-1: 345LS312 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 345LS312.

Table 720 Reliability Data Sensor Leg 1-1 345LS312

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function is quantified as follows.

Table 721 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.91E-06 | 2 | N/A | 33.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 722 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 723 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 ) Safety Instrumented Function is quantified as follows.

Table 724 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.67E-03 | 2 | N/A | 2031.38 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 5 |

#### Final Element Group 1: Close Avblödning slamvatten

The information and reliability data underneath describe the Close Avblödning slamvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avblödning slamvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV566 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 345SV566

The following table shows the equipment that defines final element leg 1-1 345SV566.

Table 725 Final Element Leg 1-1: 345SV566 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV566.

Table 726 Reliability Data Final Element Leg 1-1 345SV566

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Close Från Cyklon

The information and reliability data underneath describe the Close Från Cyklon final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Från Cyklon |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV651 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 345SV651

The following table shows the equipment that defines final element leg 1-1 345SV651.

Table 727 Final Element Leg 1-1: 345SV651 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV651.

Table 728 Reliability Data Final Element Leg 1-1 345SV651

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-062 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV634) |
| --- | --- |
| SIF Tag | SIF-062 |
| SIF Description: | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV634) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 130.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 729 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.64E-03 | 130.9 | 2 | 2 | N/A | 15.58 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 730 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.05E-04 | 3 | N/A | 228.67 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög vätskenivå WESP

The information and reliability data underneath describe the Hög vätskenivå WESP sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög vätskenivå WESP |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345LI354, 345LI355, 345LI356 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 345LI354, 345LI355, 345LI356

The following table shows the equipment that defines sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 731 Sensor Leg 1-3: 345LI354, 345LI355, 345LI356 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Enderess Hauser FMR50-57 |  | - | - | B | 3 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 732 Reliability Data Sensor Leg 1-3 345LI354, 345LI355, 345LI356

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Enderess Hauser FMR50-57 | - - | - - | - - | - - | 2.33E-06 2.33E-06 | - - | 2.49E-07 2.49E-07 | - - | - - | - - |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 733 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 734 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 735 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634) Safety Instrumented Function is quantified as follows.

Table 736 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.23E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV634 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV634

The following table shows the equipment that defines final element leg 1-1 345SV634.

Table 737 Final Element Leg 1-1: 345SV634 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV634.

Table 738 Reliability Data Final Element Leg 1-1 345SV634

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-063 SIL2 Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) |
| --- | --- |
| SIF Tag | SIF-063 |
| SIF Description: | SIL2 Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 739 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.50E-03 | 153.8 | 2 | 2 | N/A | 19.53 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function is quantified as follows.

Table 740 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345SV520, 345SV521 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 345SV520, 345SV521

The following table shows the equipment that defines sensor leg 1-2 345SV520, 345SV521.

Table 741 Sensor Leg 1-2: 345SV520, 345SV521 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 345SV520, 345SV521.

Table 742 Reliability Data Sensor Leg 1-2 345SV520, 345SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function is quantified as follows.

Table 743 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 744 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 745 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) Safety Instrumented Function is quantified as follows.

Table 746 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.29E-03 | 2 | N/A | 372.95 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV522 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV522

The following table shows the equipment that defines final element leg 1-1 345SV522.

Table 747 Final Element Leg 1-1: 345SV522 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV522.

Table 748 Reliability Data Final Element Leg 1-1 345SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | 1.46E-07 | - | 3.22E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 24.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-064 SIL2 Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) |
| --- | --- |
| SIF Tag | SIF-064 |
| SIF Description: | SIL2 Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 183.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 749 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.44E-03 | 183.8 | 2 | 2 | N/A | 20.02 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function is quantified as follows.

Table 750 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345SV520, 345SV522 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 345SV520, 345SV522

The following table shows the equipment that defines sensor leg 1-2 345SV520, 345SV522.

Table 751 Sensor Leg 1-2: 345SV520, 345SV522 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 345SV520, 345SV522.

Table 752 Reliability Data Sensor Leg 1-2 345SV520, 345SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function is quantified as follows.

Table 753 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 754 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 755 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) Safety Instrumented Function is quantified as follows.

Table 756 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.23E-03 | 2 | N/A | 708.23 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV521 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV521

The following table shows the equipment that defines final element leg 1-1 345SV521.

Table 757 Final Element Leg 1-1: 345SV521 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV521.

Table 758 Reliability Data Final Element Leg 1-1 345SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-065 SIL2 Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) |
| --- | --- |
| SIF Tag | SIF-065 |
| SIF Description: | SIL2 Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 183.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 759 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.44E-03 | 183.8 | 2 | 2 | N/A | 20.02 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function is quantified as follows.

Table 760 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345SV521, 345SV522 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 345SV521, 345SV522

The following table shows the equipment that defines sensor leg 1-2 345SV521, 345SV522.

Table 761 Sensor Leg 1-2: 345SV521, 345SV522 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 345SV521, 345SV522.

Table 762 Reliability Data Sensor Leg 1-2 345SV521, 345SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function is quantified as follows.

Table 763 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 764 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 765 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) Safety Instrumented Function is quantified as follows.

Table 766 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.23E-03 | 2 | N/A | 708.23 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV520 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV520

The following table shows the equipment that defines final element leg 1-1 345SV520.

Table 767 Final Element Leg 1-1: 345SV520 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV520.

Table 768 Reliability Data Final Element Leg 1-1 345SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-066 SIL2 Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) => Close Avstängning tillopp spolvatten (345SV634)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) => Close Avstängning tillopp spolvatten (345SV634) |
| --- | --- |
| SIF Tag | SIF-066 |
| SIF Description: | SIL2 Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) => Close Avstängning tillopp spolvatten (345SV634) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 260.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 769 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.84E-03 | 260.3 | 2 | 2 | N/A | 36.51 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function is quantified as follows.

Table 770 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.18E-05 | 3 | N/A | 3481.2 | 1 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: Tryckmätare hydrofor

The information and reliability data underneath describe the Tryckmätare hydrofor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckmätare hydrofor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345PI420, 345PI420 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-2: 345PI420, 345PI420

The following table shows the equipment that defines sensor leg 1-2 345PI420, 345PI420.

Table 771 Sensor Leg 1-2: 345PI420, 345PI420 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 345PI420, 345PI420.

Table 772 Reliability Data Sensor Leg 1-2 345PI420, 345PI420

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Tryckmätare hydrofor

The information and reliability data underneath describe the Tryckmätare hydrofor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckmätare hydrofor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ320, 320PZ320 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 320PZ320, 320PZ320, 320PZ320

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ320, 320PZ320.

Table 773 Sensor Leg 1-3: 320PZ320, 320PZ320, 320PZ320 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ320, 320PZ320.

Table 774 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ320, 320PZ320

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function is quantified as follows.

Table 775 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.79E-06 | 2 | N/A | 37.91 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 776 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 777 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

Close Avstängning tillopp spolvatten (345SV634)

Safety Instrumented Function is quantified as follows.

Table 778 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.75E-03 | 2 | N/A | 1384.78 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV634 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 345SV634

The following table shows the equipment that defines final element leg 1-1 345SV634.

Table 779 Final Element Leg 1-1: 345SV634 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV634.

Table 780 Reliability Data Final Element Leg 1-1 345SV634

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-067 SIL1 Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 Syrehalt gasväg (353AZ362¦H2) => Trip Högspänningsenhet (353EC015) |
| --- | --- |
| SIF Tag | SIF-067 |
| SIF Description: | SIL1 Syrehalt gasväg (353AZ362¦H2) => Trip Högspänningsenhet (353EC015) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 58.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 781 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.72E-02 | 58.1 | 1 | 2 | N/A | 14.4 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function is quantified as follows.

Table 782 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.30E-02 | 2 | N/A | 151.42 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Syrehalt gasväg

The information and reliability data underneath describe the Syrehalt gasväg sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Syrehalt gasväg |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353AZ362 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 72 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353AZ362

The following table shows the equipment that defines sensor leg 1-1 353AZ362.

Table 783 Sensor Leg 1-1: 353AZ362 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Siemens Sitrans SL |  | - | - | B | 1 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353AZ362.

Table 784 Reliability Data Sensor Leg 1-1 353AZ362

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Siemens Sitrans SL | - - | - - | - - | - - | 7.41E-07 7.41E-07 | - - | 1.16E-06 1.16E-06 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 39.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function is quantified as follows.

Table 785 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 786 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 787 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015) Safety Instrumented Function is quantified as follows.

Table 788 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.22E-03 | 2 | N/A | 87.89 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Högspänningsenhet

The information and reliability data underneath describe the Trip Högspänningsenhet final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Högspänningsenhet |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353EC015 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 353EC015

The following table shows the equipment that defines final element leg 1-1 353EC015.

Table 789 Final Element Leg 1-1: 353EC015 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic MCC - interrupt function 10 < HP <=100 | 2012.Q3.02 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353EC015.

Table 790 Reliability Data Final Element Leg 1-1 353EC015

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic MCC - interrupt function 10 < HP <=100 | - | 1.20E-06 | - | 7.20E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 64.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-068 SIL2 Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 )

This chapter details the SIL Verification results, selections, and assumptions for the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) |
| --- | --- |
| SIF Tag | SIF-068 |
| SIF Description: | SIL2 Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 133.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 791 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.47E-03 | 133.8 | 2 | 2 | N/A | 18.87 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function is quantified as follows.

Table 792 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.65E-04 | 2 | N/A | 10364.55 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Vätsketryck nedströms pump

The information and reliability data underneath describe the Vätsketryck nedströms pump sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätsketryck nedströms pump |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353PI326 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353PI326

The following table shows the equipment that defines sensor leg 1-1 353PI326.

Table 793 Sensor Leg 1-1: 353PI326 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353PI326.

Table 794 Reliability Data Sensor Leg 1-1 353PI326

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 88.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Vätsketryck nedströms pump

The information and reliability data underneath describe the Vätsketryck nedströms pump sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätsketryck nedströms pump |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 320PZ320, 320PZ321, 320PZ322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322

The following table shows the equipment that defines sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 795 Sensor Leg 1-3: 320PZ320, 320PZ321, 320PZ322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 320PZ320, 320PZ321, 320PZ322.

Table 796 Reliability Data Sensor Leg 1-3 320PZ320, 320PZ321, 320PZ322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function is quantified as follows.

Table 797 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.42E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 798 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 799 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) Safety Instrumented Function is quantified as follows.

Table 800 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-03 | 2 | N/A | 709.28 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avblödning slamvatten

The information and reliability data underneath describe the Close Avblödning slamvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avblödning slamvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV566 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 353SV566

The following table shows the equipment that defines final element leg 1-1 353SV566.

Table 801 Final Element Leg 1-1: 353SV566 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353SV566.

Table 802 Reliability Data Final Element Leg 1-1 353SV566

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-069 SIL2 Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätskenivå sludge tank (353LS310¦H2) => Close Avstängning tillopp spolvatten (345SV635) |
| --- | --- |
| SIF Tag | SIF-069 |
| SIF Description: | SIL2 Vätskenivå sludge tank (353LS310¦H2) => Close Avstängning tillopp spolvatten (345SV635) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 126.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 803 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.90E-03 | 126.5 | 2 | 2 | N/A | 18.31 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 804 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.69E-04 | 2 | N/A | 576.96 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Vätskenivå sludge tank

The information and reliability data underneath describe the Vätskenivå sludge tank sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätskenivå sludge tank |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353LS310 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353LS310

The following table shows the equipment that defines sensor leg 1-1 353LS310.

Table 805 Sensor Leg 1-1: 353LS310 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353LS310.

Table 806 Reliability Data Sensor Leg 1-1 353LS310

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 77.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 807 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 808 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 809 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 810 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.23E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV635 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV635

The following table shows the equipment that defines final element leg 1-1 345SV635.

Table 811 Final Element Leg 1-1: 345SV635 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV635.

Table 812 Reliability Data Final Element Leg 1-1 345SV635

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-070 SIL2 Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 )

This chapter details the SIL Verification results, selections, and assumptions for the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Vätskenivå sludge tank (353LS312¦L2) => Close Avblödning slamvatten (353SV566 ) |
| --- | --- |
| SIF Tag | SIF-070 |
| SIF Description: | SIL2 Vätskenivå sludge tank (353LS312¦L2) => Close Avblödning slamvatten (353SV566 ) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 124.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 813 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.05E-03 | 124.2 | 2 | 2 | N/A | 18.35 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function is quantified as follows.

Table 814 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.22E-04 | 2 | N/A | 621.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Vätskenivå sludge tank

The information and reliability data underneath describe the Vätskenivå sludge tank sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätskenivå sludge tank |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353LS312 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 353LS312

The following table shows the equipment that defines sensor leg 1-1 353LS312.

Table 815 Sensor Leg 1-1: 353LS312 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 353LS312.

Table 816 Reliability Data Sensor Leg 1-1 353LS312

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function is quantified as follows.

Table 817 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 818 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 819 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 ) Safety Instrumented Function is quantified as follows.

Table 820 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.23E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avblödning slamvatten

The information and reliability data underneath describe the Close Avblödning slamvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avblödning slamvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV566 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV566

The following table shows the equipment that defines final element leg 1-1 345SV566.

Table 821 Final Element Leg 1-1: 345SV566 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV566.

Table 822 Reliability Data Final Element Leg 1-1 345SV566

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-071 SIL2 Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Hög vätskenivå WESP (353LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV635) |
| --- | --- |
| SIF Tag | SIF-071 |
| SIF Description: | SIL2 Hög vätskenivå WESP (353LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV635) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 130.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 823 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.64E-03 | 130.9 | 2 | 2 | N/A | 15.58 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 824 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.05E-04 | 3 | N/A | 228.67 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög vätskenivå WESP

The information and reliability data underneath describe the Hög vätskenivå WESP sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög vätskenivå WESP |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353LI354, 353LI355, 353LI356 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 353LI354, 353LI355, 353LI356

The following table shows the equipment that defines sensor leg 1-3 353LI354, 353LI355, 353LI356.

Table 825 Sensor Leg 1-3: 353LI354, 353LI355, 353LI356 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Enderess Hauser FMR50-57 |  | - | - | B | 3 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 353LI354, 353LI355, 353LI356.

Table 826 Reliability Data Sensor Leg 1-3 353LI354, 353LI355, 353LI356

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Enderess Hauser FMR50-57 | - - | - - | - - | - - | 2.33E-06 2.33E-06 | - - | 2.49E-07 2.49E-07 | - - | - - | - - |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 827 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 828 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 829 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635) Safety Instrumented Function is quantified as follows.

Table 830 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.23E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV635 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV635

The following table shows the equipment that defines final element leg 1-1 345SV635.

Table 831 Final Element Leg 1-1: 345SV635 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV635.

Table 832 Reliability Data Final Element Leg 1-1 345SV635

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-072 SIL2 Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) |
| --- | --- |
| SIF Tag | SIF-072 |
| SIF Description: | SIL2 Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 833 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.50E-03 | 153.8 | 2 | 2 | N/A | 19.53 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function is quantified as follows.

Table 834 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353SV520, 353SV521 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 353SV520, 353SV521

The following table shows the equipment that defines sensor leg 1-2 353SV520, 353SV521.

Table 835 Sensor Leg 1-2: 353SV520, 353SV521 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 353SV520, 353SV521.

Table 836 Reliability Data Sensor Leg 1-2 353SV520, 353SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function is quantified as follows.

Table 837 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 838 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 839 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) Safety Instrumented Function is quantified as follows.

Table 840 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.29E-03 | 2 | N/A | 372.95 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV522 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 353SV522

The following table shows the equipment that defines final element leg 1-1 353SV522.

Table 841 Final Element Leg 1-1: 353SV522 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353SV522.

Table 842 Reliability Data Final Element Leg 1-1 353SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | 1.46E-07 | - | 3.22E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 24.0 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-073 SIL2 Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) |
| --- | --- |
| SIF Tag | SIF-073 |
| SIF Description: | SIL2 Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 183.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 843 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.44E-03 | 183.8 | 2 | 2 | N/A | 20.02 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function is quantified as follows.

Table 844 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353SV520, 353SV522 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 353SV520, 353SV522

The following table shows the equipment that defines sensor leg 1-2 353SV520, 353SV522.

Table 845 Sensor Leg 1-2: 353SV520, 353SV522 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 353SV520, 353SV522.

Table 846 Reliability Data Sensor Leg 1-2 353SV520, 353SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function is quantified as follows.

Table 847 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 848 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 849 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) Safety Instrumented Function is quantified as follows.

Table 850 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.23E-03 | 2 | N/A | 708.23 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV521 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 353SV521

The following table shows the equipment that defines final element leg 1-1 353SV521.

Table 851 Final Element Leg 1-1: 353SV521 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353SV521.

Table 852 Reliability Data Final Element Leg 1-1 353SV521

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-074 SIL2 Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) |
| --- | --- |
| SIF Tag | SIF-074 |
| SIF Description: | SIL2 Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 183.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 853 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.44E-03 | 183.8 | 2 | 2 | N/A | 20.02 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function is quantified as follows.

Table 854 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.02E-04 | 2 | N/A | 40131.7 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Position avstängning venturihals

The information and reliability data underneath describe the Position avstängning venturihals sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Position avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 353SV521, 353SV522 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 353SV521, 353SV522

The following table shows the equipment that defines sensor leg 1-2 353SV521, 353SV522.

Table 855 Sensor Leg 1-2: 353SV521, 353SV522 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| KControls 007 |  | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 353SV521, 353SV522.

Table 856 Reliability Data Sensor Leg 1-2 353SV521, 353SV522

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| KControls 007 | - - | - - | - - | - - | 1.78E-08 1.78E-08 | - - | 1.80E-08 1.80E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 71.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function is quantified as follows.

Table 857 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 858 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 859 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) Safety Instrumented Function is quantified as follows.

Table 860 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.23E-03 | 2 | N/A | 708.23 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open avstängning venturihals

The information and reliability data underneath describe the Open avstängning venturihals final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open avstängning venturihals |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 353SV520 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 353SV520

The following table shows the equipment that defines final element leg 1-1 353SV520.

Table 861 Final Element Leg 1-1: 353SV520 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 353SV520.

Table 862 Reliability Data Final Element Leg 1-1 353SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 16.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) |
| --- | --- |
| SIF Tag | SIF-075 |
| SIF Description: | SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 135.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 863 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.36E-03 | 135.8 | 2 | 2 | N/A | 18.88 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function is quantified as follows.

Table 864 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.37E-04 | 3 | N/A | 10637.24 | 1 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck

The information and reliability data underneath describe the Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ323, 253PZ324, 253PZ325 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 253PZ323, 253PZ324, 253PZ325

The following table shows the equipment that defines sensor leg 1-3 253PZ323, 253PZ324, 253PZ325.

Table 865 Sensor Leg 1-3: 253PZ323, 253PZ324, 253PZ325 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 253PZ323, 253PZ324, 253PZ325.

Table 866 Reliability Data Sensor Leg 1-3 253PZ323, 253PZ324, 253PZ325

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck

The information and reliability data underneath describe the Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PZ305, 343PZ307, 343PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308

The following table shows the equipment that defines sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 867 Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 868 Reliability Data Sensor Leg 1-3 343PZ305, 343PZ307, 343PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function is quantified as follows.

Table 869 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 870 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 871 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) Safety Instrumented Function is quantified as follows.

Table 872 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.82E-03 | 2 | N/A | 712.14 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close N2 till reduktionskrets

The information and reliability data underneath describe the Close N2 till reduktionskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close N2 till reduktionskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV582 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 254SV582

The following table shows the equipment that defines final element leg 1-1 254SV582.

Table 873 Final Element Leg 1-1: 254SV582 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV582.

Table 874 Reliability Data Final Element Leg 1-1 254SV582

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-076 SIL2 Hög nivå i ångpanna 271AG001 (271LZ316|H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Hög nivå i ångpanna 271AG001 (271LZ316¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) |
| --- | --- |
| SIF Tag | SIF-076 |
| SIF Description: | SIL2 Hög nivå i ångpanna 271AG001 (271LZ316¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 122.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 875 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.15E-03 | 122.7 | 2 | 2 | N/A | 21.61 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function is quantified as follows.

Table 876 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.58E-04 | 2 | N/A | 3060.49 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög nivå i ångpanna 271AG001

The information and reliability data underneath describe the Hög nivå i ångpanna 271AG001 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög nivå i ångpanna 271AG001 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 271LZ316 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 271LZ316

The following table shows the equipment that defines sensor leg 1-1 271LZ316.

Table 877 Sensor Leg 1-1: 271LZ316 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Gestra NRS 1-50 |  | - | - | B | - |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 271LZ316.

Table 878 Reliability Data Sensor Leg 1-1 271LZ316

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Gestra NRS 1-50 | - - | - - | - - | - - | 3.73E-08 3.73E-08 | - - | 2.69E-08 2.69E-08 | - - | - - | - - |
|  |  |  |  |  |  |  | SFF [%] |  |  | 58.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function is quantified as follows.

Table 879 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.24E-06 | 2 | N/A | 22.45 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 880 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 881 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) Safety Instrumented Function is quantified as follows.

Table 882 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 883 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 884 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) => Close Avstängningsventil O2 efter tankpark (251SV520)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Temp efter O2-förångare vid tankparken (251TI300 ¦L2) => Close Avstängningsventil O2 efter tankpark (251SV520) |
| --- | --- |
| SIF Tag | SIF-077 |
| SIF Description: | Temp efter O2-förångare vid tankparken (251TI300 ¦L2) => Close Avstängningsventil O2 efter tankpark (251SV520) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 108.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 885 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 9.19E-03 | 108.8 | 2 | 2 | N/A | 18.24 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function is quantified as follows.

Table 886 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 513.5 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp efter O2-förångare vid tankparken

The information and reliability data underneath describe the Temp efter O2-förångare vid tankparken sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp efter O2-förångare vid tankparken |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 251TI300 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 251TI300

The following table shows the equipment that defines sensor leg 1-1 251TI300.

Table 887 Sensor Leg 1-1: 251TI300 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 251TI300.

Table 888 Reliability Data Sensor Leg 1-1 251TI300

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 67.7 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function is quantified as follows.

Table 889 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 890 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 891 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

Close Avstängningsventil O2 efter tankpark (251SV520) Safety Instrumented Function is quantified as follows.

Table 892 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängningsventil O2 efter tankpark

The information and reliability data underneath describe the Close Avstängningsventil O2 efter tankpark final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängningsventil O2 efter tankpark |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV520 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 251SV520

The following table shows the equipment that defines final element leg 1-1 251SV520.

Table 893 Final Element Leg 1-1: 251SV520 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 251SV520.

Table 894 Reliability Data Final Element Leg 1-1 251SV520

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631

This chapter details the SIL Verification results, selections, and assumptions for the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 |
| --- | --- |
| SIF Tag | SIF-078 |
| SIF Description: | SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 0 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 0 with RRF = 0 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 28 Apr 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61508 |
| Consider Systematic Capability: | Yes |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 895 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61508 | Systematic Capability |  |
| 0.00E+00 | 0 | 0 | 0 | 0 | ∞ |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function is quantified as follows.

Table 896 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 3.85E-04 | 2 | 2 | 93.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: SIL2 253PZ352 (TRYCKMÄTNING 320YM005)

The information and reliability data underneath describe the SIL2 253PZ352 (TRYCKMÄTNING 320YM005) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIL2 253PZ352 (TRYCKMÄTNING 320YM005) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ352 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 253PZ352

The following table shows the equipment that defines sensor leg 1-1 253PZ352.

Table 897 Sensor Leg 1-1: 253PZ352 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 253PZ352.

Table 898 Reliability Data Sensor Leg 1-1 253PZ352

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function is quantified as follows.

Table 899 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | 2 | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 900 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | 2 |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 901 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 Safety Instrumented Function is quantified as follows.

Table 902 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61508 | Systematic Capability |  |  |  |
| 0.00E+00 | 0 | 0 | ∞ | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close 253SV631

The information and reliability data underneath describe the Close 253SV631 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 253SV631 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: |  |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

# SIF-079 SIL2 341PZ401 (H2/L2) => close H2

This chapter details the SIL Verification results, selections, and assumptions for the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 341PZ401 (H2/L2) => close H2 |
| --- | --- |
| SIF Tag | SIF-079 |
| SIF Description: | SIL2 252PZ337 (H2/L2) => Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 151.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 903 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.59E-03 | 151.6 | 2 | 2 | N/A | 27.36 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function is quantified as follows.

Table 904 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.58E-04 | 2 | N/A | 533.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Vätgastryck till brännare

The information and reliability data underneath describe the Vätgastryck till brännare sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Vätgastryck till brännare |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PZ401 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 341PZ401

The following table shows the equipment that defines sensor leg 1-1 341PZ401.

Table 905 Sensor Leg 1-1: 341PZ401 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PZ401.

Table 906 Reliability Data Sensor Leg 1-1 341PZ401

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function is quantified as follows.

Table 907 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.05E-06 | 2 | N/A | 29.3 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 908 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 909 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2 Safety Instrumented Function is quantified as follows.

Table 910 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.24E-03 | 2 | N/A | 1825.59 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: H2 till brännare PGH

The information and reliability data underneath describe the H2 till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2 till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV665, 341SV667 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 341SV665, 341SV667

The following table shows the equipment that defines final element leg 1-2 341SV665, 341SV667.

Table 911 Final Element Leg 1-2: 341SV665, 341SV667 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 341SV665, 341SV667.

Table 912 Reliability Data Final Element Leg 1-2 341SV665, 341SV667

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängning O2

The information and reliability data underneath describe the Avstängning O2 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Beta Estimator Selections

The following selections were made as part of the beta estimator for the Avstängning O2 final element group.

| Separation/Segregation |  |
| --- | --- |
| Description | Yes/No |
| Are all signal cables for the channels routed separately at all positions? | No |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel on separate printed-circuit boards? | Yes |
| If the sensors/final elements have dedicated control electronics, is the electronics for each channel indoors and in separate cabinets? | No |
| Diversity/Redundancy |  |
| Description | Yes/No |
| Do the devices employ different physical principles for the sensing elements for example, pressure and temperature, vane anemometer and Doppler transducer, etc? | No |
| Do the devices employ different electrical principles/designs for example, digital and analogue, different manufacturer (not re-badged) or different technology? | No |
| Are separate test methods and people used for each channel during commissioning? | No |
| Is maintenance on each channel carried out by different people at different times? | No |
| Complexity/Design/Application/Maturity/Experience |  |
| Description | Yes/No |
| Does cross-connection between channels preclude the exchange of any information other than that used for diagnostic testing or voting purposes? | Yes |
| Is the design based on techniques used in equipment that has been used successfully in the field for > 5 years? | Yes |
| Is there more than 5 years experience with the same hardware used in similar environments? | Yes |
| Are inputs and outputs protected from potential levels of over-voltage and over-current? | Yes |
| Are all devices/components conservatively rated (for example, by a factor of 2 or more)? | No |
| Assessment/Analysis and Feedback of Data |  |
| Description | Yes/No |
| Have the results of the failure modes and effects analysis or fault-tree analysis been examined to establish sources of common cause failure and have predetermined sources of common cause failure been eliminated by design? | Yes |
| Were common cause failures considered in design reviews with the results fed back into the design? (Documentary evidence of the design review activity is required.) | No |
| Are all field failures fully analyzed with feedback into the design? (Documentary evidence of the procedure is required.) | No |
| Procedures/Human Interface |  |
| Description | Yes/No |
| Is there a written system of work to ensure that all component failures (or degradations) are detected, the root causes established and other similar items inspected for similar potential causes of failure? | Yes |
| Are procedures in place to ensure that: maintenance (including adjustment or calibration) of any part of the independent channels is staggered, and, in addition to the manual checks carried out following maintenance, the diagnostic tests are allowed to run satisfactorily between the completion of maintenance on one channel and the start of maintenance on another? | Yes |
| Do the documented maintenance procedures specify that all parts of redundant systems (for example, cables, etc.) intended to be independent of each other, are not to be relocated? | No |
| Is all maintenance of printed-circuit boards, etc. carried out off-site at a qualified repair centre and have all the repaired items gone through a full pre-installation testing? | Yes |
| Do the system diagnostic tests report failures to the level of a field-replaceable module? | Yes |
| Competence/Training/Safety Culture |  |
| Description | Yes/No |
| Have designers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Have maintainers been trained (with training documentation) to understand the causes and consequences of common cause failures? | No |
| Environmental Control |  |
| Description | Yes/No |
| Is personnel access limited (for example locked cabinets, inaccessible position)? | No |
| Is the system likely to operate always within the range of temperature, humidity, corrosion, dust, vibration, etc., over which it has been tested, without the use of external environmental control? | Yes |
| Are all signal and power cables separate at all positions? | No |
| Environmental Testing |  |
| Description | Yes/No |
| Has the system been tested for immunity to all relevant environmental influences (for example EMC, temperature, vibration, shock, humidity) to an appropriate level as specified in recognized standards? | No |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 913 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 914 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 3: Avstängningsventil 2 överhettad ånga till PGH PT 6

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH PT 6 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH PT 6 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 915 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 916 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

This chapter details the SIL Verification results, selections, and assumptions for the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556 |
| --- | --- |
| SIF Tag | SIF-080 |
| SIF Description: | SIL1 271XI323 Ånga ej tillräckligt överhettad => permissive 271SV556 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 68.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 28 Apr 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 917 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.46E-02 | 68.6 | 1 | 2 | N/A | 18.9 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function is quantified as follows.

Table 918 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.63E-03 | 2 | N/A | 50602.91 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Ånga ej tillräckligt överhettad

The information and reliability data underneath describe the Ånga ej tillräckligt överhettad sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Ånga ej tillräckligt överhettad |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 271TI322, 271PI320 |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 93.4 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1: 271TI322

The following table shows the equipment that defines sensor leg 1 271TI322.

Table 919 Sensor Leg 1: 271TI322 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 271TI322.

Table 920 Reliability Data Sensor Leg 1 271TI322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - - | - - | 1.07E-07 3.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 7.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 271PI320

The following table shows the equipment that defines sensor leg 2 271PI320.

Table 921 Sensor Leg 2: 271PI320 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 271PI320.

Table 922 Reliability Data Sensor Leg 2 271PI320

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function is quantified as follows.

Table 923 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 924 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 925 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

Safety Instrumented Function is quantified as follows.

Table 926 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängningsventil 2 överhettad ånga till PGH

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 927 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 928 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K

This chapter details the SIL Verification results, selections, and assumptions for the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K |
| --- | --- |
| SIF Tag | SIF-081 |
| SIF Description: | SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 254.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 929 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.93E-03 | 254.5 | 2 | 2 | N/A | 16.33 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function is quantified as follows.

Table 930 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.89E-03 | 2 | N/A | 5138.39 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Mätvärde på tillsatt flöde naturgas

The information and reliability data underneath describe the Mätvärde på tillsatt flöde naturgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Mätvärde på tillsatt flöde naturgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 252PD565, 252TI565, 252PI565 |
| Voting within group: | 3oo3 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1: 252PD565

The following table shows the equipment that defines sensor leg 1 252PD565.

Table 931 Sensor Leg 1: 252PD565 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 252PD565.

Table 932 Reliability Data Sensor Leg 1 252PD565

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.89E-08 6.89E-08 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 87.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 252TI565

The following table shows the equipment that defines sensor leg 2 252TI565.

Table 933 Sensor Leg 2: 252TI565 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 252TI565.

Table 934 Reliability Data Sensor Leg 2 252TI565

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 67.7 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 3: 252PI565

The following table shows the equipment that defines sensor leg 3 252PI565.

Table 935 Sensor Leg 3: 252PI565 Details

| Sensor Leg 3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 3 252PI565.

Table 936 Reliability Data Sensor Leg 3 252PI565

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 88.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function is quantified as follows.

Table 937 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 938 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 939 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K Safety Instrumented Function is quantified as follows.

Table 940 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.04E-03 | 3 | N/A | 378.21 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 941 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 942 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-082 SIL2 252PZ337 (H2/L2) => close NG

This chapter details the SIL Verification results, selections, and assumptions for the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 252PZ337 (H2/L2) => close NG |
| --- | --- |
| SIF Tag | SIF-082 |
| SIF Description: | SIL2 252PZ337 (H2/L2) => Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 560.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 943 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.78E-03 | 560.9 | 2 | 2 | N/A | 33.78 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function is quantified as follows.

Table 944 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.58E-04 | 2 | N/A | 533.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Naturgastryck till brännare

The information and reliability data underneath describe the Naturgastryck till brännare sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Naturgastryck till brännare |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | Sensor Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: Sensor Leg

The following table shows the equipment that defines sensor leg 1-1 Sensor Leg.

Table 945 Sensor Leg 1-1: Sensor Leg Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 Sensor Leg.

Table 946 Reliability Data Sensor Leg 1-1 Sensor Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function is quantified as follows.

Table 947 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.79E-06 | 2 | N/A | 37.91 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 948 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 949 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG Safety Instrumented Function is quantified as follows.

Table 950 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.42E-03 | 3 | N/A | 741.34 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: NG till brännare PGH

The information and reliability data underneath describe the NG till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 951 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 952 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | Beräkning difftryck 253XI364¦L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) |
| --- | --- |
| SIF Tag | SIF-083 |
| SIF Description: | SIL2 Beräkning difftryck 253XI364 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) => Close kvävgasventil 1 O2 inj. (253SV651 SIL2) Close avstängningsventil mot O2-lans inj. (251SV562 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 0 with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 369.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 953 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.71E-03 | 369.2 | 2 | 2 | N/A | 18.3 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 954 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.94E-04 | 2 | N/A | 1886.25 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: Difftryck N2

The information and reliability data underneath describe the Difftryck N2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Difftryck N2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 253PZ362, 253PZ363, 253PZ364 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364

The following table shows the equipment that defines sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 955 Sensor Leg 1-3: 253PZ362, 253PZ363, 253PZ364 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 253PZ362, 253PZ363, 253PZ364.

Table 956 Reliability Data Sensor Leg 1-3 253PZ362, 253PZ363, 253PZ364

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Gastryck transferline

The information and reliability data underneath describe the Gastryck transferline sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastryck transferline |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344PZ321 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344PZ321

The following table shows the equipment that defines sensor leg 1-1 344PZ321.

Table 957 Sensor Leg 1-1: 344PZ321 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344PZ321.

Table 958 Reliability Data Sensor Leg 1-1 344PZ321

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 959 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 960 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 961 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) Safety Instrumented Function is quantified as follows.

Table 962 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.81E-03 | 3 | N/A | 377.66 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 963 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 964 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6¦H2) |
| --- | --- |
| SIF Tag | SIF-084 |
| SIF Description: | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) => Trip Processgaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 309.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: | IEC 61511 - Functional safety: Safety Instrumented Systems for the Process Industry Sector |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 965 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.23E-03 | 309.4 | 2 | 2 | N/A | 17.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 966 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.05E-04 | 3 | N/A | 228.67 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Hög vätskenivå WESP

The information and reliability data underneath describe the Hög vätskenivå WESP sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Hög vätskenivå WESP |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345LI354, 345LI355, 345LI356 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 345LI354, 345LI355, 345LI356

The following table shows the equipment that defines sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 967 Sensor Leg 1-3: 345LI354, 345LI355, 345LI356 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Enderess Hauser FMR50-57 |  | - | - | B | 3 |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 345LI354, 345LI355, 345LI356.

Table 968 Reliability Data Sensor Leg 1-3 345LI354, 345LI355, 345LI356

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Enderess Hauser FMR50-57 | - - | - - | - - | - - | 2.33E-06 2.33E-06 | - - | 2.49E-07 2.49E-07 | - - | - - | - - |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 969 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 970 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 971 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2) Safety Instrumented Function is quantified as follows.

Table 972 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.82E-03 | 2 | N/A | 1095.95 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Trip red.gaskompressor

The information and reliability data underneath describe the Trip red.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 346PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 346PU101

The following table shows the equipment that defines final element leg 1-1 346PU101.

Table 973 Final Element Leg 1-1: 346PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 346PU101.

Table 974 Reliability Data Final Element Leg 1-1 346PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Leak Test; Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 975 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 976 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift (344MA001_RUN_N)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Reduktionsgasvärmare trip/ej i drift (344MA001_RUN_N) |
| --- | --- |
| SIF Tag | SIF-085 |
| SIF Description: | SIL2 Reduktionsgasvärmare trip/ej i drift (344MA001_RUN_N) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 ) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 111.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: | IEC 61511 - Functional safety: Safety Instrumented Systems for the Process Industry Sector |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 977 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.98E-03 | 111.3 | 2 | 2 | N/A | 33.87 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function is quantified as follows.

Table 978 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.15E-03 | 2 | N/A | 31371.67 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Reduktionsgasvärmare trip/ej i drift

The information and reliability data underneath describe the Reduktionsgasvärmare trip/ej i drift sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Reduktionsgasvärmare trip/ej i drift |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 252HV548 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 252HV548

The following table shows the equipment that defines sensor leg 1-1 252HV548.

Table 979 Sensor Leg 1-1: 252HV548 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Quarts QN45 |  | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 252HV548.

Table 980 Reliability Data Sensor Leg 1-1 252HV548

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Quarts QN45 | 3.55E-07 - | - - | 1.11E-07 - | - - | - - | - - | 1.11E-07 5.77E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 4.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Reduktionsgasvärmare trip/ej i drift

The information and reliability data underneath describe the Reduktionsgasvärmare trip/ej i drift sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Reduktionsgasvärmare trip/ej i drift |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | Sensor Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: Sensor Leg

The following table shows the equipment that defines sensor leg 1-1 Sensor Leg.

Table 981 Sensor Leg 1-1: Sensor Leg Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Quarts QN45 |  | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 Sensor Leg.

Table 982 Reliability Data Sensor Leg 1-1 Sensor Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Quarts QN45 | 3.55E-07 - | - - | 1.11E-07 - | - - | - - | - - | 1.11E-07 5.77E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 4.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function is quantified as follows.

Table 983 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.45E-06 | 2 | N/A | 34.63 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 984 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 985 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

Safety Instrumented Function is quantified as follows.

Table 986 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.87E-03 | 2 | N/A | 1638.37 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Avstängning O2 PT12

The information and reliability data underneath describe the Avstängning O2 PT12 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängning O2 PT12 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Leak Test; Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 987 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 988 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

#### Final Element Group 2: Avstängningsventil 2 överhettad ånga till PGH PT 6

The information and reliability data underneath describe the Avstängningsventil 2 överhettad ånga till PGH PT 6 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Avstängningsventil 2 överhettad ånga till PGH PT 6 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 271SV556 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: 271SV556

The following table shows the equipment that defines final element leg 1-1 271SV556.

Table 989 Final Element Leg 1-1: 271SV556 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 271SV556.

Table 990 Reliability Data Final Element Leg 1-1 271SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH) => Stop electrolyzer A

This chapter details the SIL Verification results, selections, and assumptions for the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Temperature H2 A (341TZ300 TZA HH) => Stop electrolyzer A |
| --- | --- |
| SIF Tag | SIF-086 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 145.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 991 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.85E-03 | 145.9 | 2 | 2 | N/A | 17.7 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 992 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Luttemperatur H2 A

The information and reliability data underneath describe the Luttemperatur H2 A sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Luttemperatur H2 A |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 3411TZ300 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 3411TZ300

The following table shows the equipment that defines sensor leg 1-1 3411TZ300.

Table 993 Sensor Leg 1-1: 3411TZ300 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 3411TZ300.

Table 994 Reliability Data Sensor Leg 1-1 3411TZ300

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 995 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 996 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 997 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 998 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 999 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1000 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH) => Stop electrolyzer A

This chapter details the SIL Verification results, selections, and assumptions for the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Temperature O2 A (341TZ303 TZA HH) => Stop electrolyzer A |
| --- | --- |
| SIF Tag | SIF-087 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 145.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1001 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.85E-03 | 145.9 | 2 | 2 | N/A | 17.7 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1002 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Luttemperatur O2 A

The information and reliability data underneath describe the Luttemperatur O2 A sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Luttemperatur O2 A |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341TZ303 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341TZ303

The following table shows the equipment that defines sensor leg 1-1 341TZ303.

Table 1003 Sensor Leg 1-1: 341TZ303 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341TZ303.

Table 1004 Reliability Data Sensor Leg 1-1 341TZ303

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1005 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1006 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1007 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1008 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1009 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1010 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH) => Stop electrolyzer B

This chapter details the SIL Verification results, selections, and assumptions for the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Temperature H2 B (341TZ320 TZA HH) => Stop electrolyzer B |
| --- | --- |
| SIF Tag | SIF-088 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 145.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1011 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.85E-03 | 145.9 | 2 | 2 | N/A | 17.7 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function is quantified as follows.

Table 1012 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Luttemperatur H2 B

The information and reliability data underneath describe the Luttemperatur H2 B sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Luttemperatur H2 B |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341TZ320 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341TZ320

The following table shows the equipment that defines sensor leg 1-1 341TZ320.

Table 1013 Sensor Leg 1-1: 341TZ320 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341TZ320.

Table 1014 Reliability Data Sensor Leg 1-1 341TZ320

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function is quantified as follows.

Table 1015 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1016 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1017 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B Safety Instrumented Function is quantified as follows.

Table 1018 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1019 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1020 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH) => Stop electrolyzer B

This chapter details the SIL Verification results, selections, and assumptions for the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Temperature O2 B (341TZ323 TZA HH) => Stop electrolyzer B |
| --- | --- |
| SIF Tag | SIF-089 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 145.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1021 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.85E-03 | 145.9 | 2 | 2 | N/A | 17.7 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1022 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Luttemperatur O2 B

The information and reliability data underneath describe the Luttemperatur O2 B sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Luttemperatur O2 B |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341TZ323 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341TZ323

The following table shows the equipment that defines sensor leg 1-1 341TZ323.

Table 1023 Sensor Leg 1-1: 341TZ323 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341TZ323.

Table 1024 Reliability Data Sensor Leg 1-1 341TZ323

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1025 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1026 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1027 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1028 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1029 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1030 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL) => Stop electrolyzer A

This chapter details the SIL Verification results, selections, and assumptions for the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL) => Stop electrolyzer A |
| --- | --- |
| SIF Tag | SIF-090 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 167.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1031 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.98E-03 | 167.1 | 2 | 2 | N/A | 17.48 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1032 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.37E-04 | 2 | N/A | 108.08 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: O2 Separator A Level transmitter 2

The information and reliability data underneath describe the O2 Separator A Level transmitter 2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 Separator A Level transmitter 2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LZ306 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LZ306

The following table shows the equipment that defines sensor leg 1-1 341LZ306.

Table 1033 Sensor Leg 1-1: 341LZ306 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| WIKA |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LZ306.

Table 1034 Reliability Data Sensor Leg 1-1 341LZ306

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| WIKA | - - | - - | - - | - - | 2.80E-07 2.80E-07 | - - | 2.97E-08 2.97E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 97.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1035 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1036 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1037 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1038 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1039 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1040 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL) => Stop electrolyzer B

This chapter details the SIL Verification results, selections, and assumptions for the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL) => Stop electrolyzer B |
| --- | --- |
| SIF Tag | SIF-091 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 167.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1041 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.98E-03 | 167.1 | 2 | 2 | N/A | 17.48 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1042 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.37E-04 | 2 | N/A | 108.08 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: O2 Separator B Level Transmitter 2

The information and reliability data underneath describe the O2 Separator B Level Transmitter 2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 Separator B Level Transmitter 2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LZ326 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LZ326

The following table shows the equipment that defines sensor leg 1-1 341LZ326.

Table 1043 Sensor Leg 1-1: 341LZ326 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| WIKA |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LZ326.

Table 1044 Reliability Data Sensor Leg 1-1 341LZ326

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| WIKA | - - | - - | - - | - - | 2.80E-07 2.80E-07 | - - | 2.97E-08 2.97E-08 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 97.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1045 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1046 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1047 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1048 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1049 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1050 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer A and successfull nitrogen purging

This chapter details the SIL Verification results, selections, and assumptions for the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer A and successfull nitrogen purging |
| --- | --- |
| SIF Tag | SIF-092 |
| SIF Description: | ESD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 31 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1051 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.22E-02 | 31 | 1 | 2 | N/A | 24.53 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1052 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.90E-03 | 2 | N/A | 306.91 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: O2 in H2 A analyzer

The information and reliability data underneath describe the O2 in H2 A analyzer sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 in H2 A analyzer |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341QZ319 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341QZ319

The following table shows the equipment that defines sensor leg 1-1 341QZ319.

Table 1053 Sensor Leg 1-1: 341QZ319 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Servomex gas analyzer |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341QZ319.

Table 1054 Reliability Data Sensor Leg 1-1 341QZ319

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Servomex gas analyzer | - - | - - | - - | - - | - - | - - | 4.34E-07 4.34E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 65.3 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1055 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1056 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1057 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1058 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.74E-02 | 2 | N/A | 1843.7 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: Kvävgas till Vätgastank A (open)

The information and reliability data underneath describe the Kvävgas till Vätgastank A (open) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank A (open) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV665, 254SV663 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV665, 254SV663

The following table shows the equipment that defines final element leg 1-2 254SV665, 254SV663.

Table 1059 Final Element Leg 1-2: 254SV665, 254SV663 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV665, 254SV663.

Table 1060 Reliability Data Final Element Leg 1-2 254SV665, 254SV663

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Kvävgas till Vätgastank A (close)

The information and reliability data underneath describe the Kvävgas till Vätgastank A (close) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank A (close) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV664 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 254SV664

The following table shows the equipment that defines final element leg 1-1 254SV664.

Table 1061 Final Element Leg 1-1: 254SV664 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV664.

Table 1062 Reliability Data Final Element Leg 1-1 254SV664

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1063 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1064 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH) => Stop electrolyzer B and successfull nitrogen purging

This chapter details the SIL Verification results, selections, and assumptions for the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ O2 in H2 B Analyzer (341QZ339 QA HH) => Stop electrolyzer B and successfull nitrogen purging |
| --- | --- |
| SIF Tag | SIF-093 |
| SIF Description: | ESD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 31 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1065 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.22E-02 | 31 | 1 | 2 | N/A | 24.53 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1066 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.90E-03 | 2 | N/A | 306.91 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: O2 in H2 B Analyzer

The information and reliability data underneath describe the O2 in H2 B Analyzer sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 in H2 B Analyzer |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341QZ339 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341QZ339

The following table shows the equipment that defines sensor leg 1-1 341QZ339.

Table 1067 Sensor Leg 1-1: 341QZ339 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Servomex gas analyzer |  | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341QZ339.

Table 1068 Reliability Data Sensor Leg 1-1 341QZ339

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Servomex gas analyzer | - - | - - | - - | - - | - - | - - | 4.34E-07 4.34E-07 | - - | - - | - - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 65.3 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1069 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1070 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1071 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1072 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.74E-02 | 2 | N/A | 1843.7 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1073 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1074 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Kvävgas till Vätgastank B (open)

The information and reliability data underneath describe the Kvävgas till Vätgastank B (open) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank B (open) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV675, 254SV673 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV675, 254SV673

The following table shows the equipment that defines final element leg 1-2 254SV675, 254SV673.

Table 1075 Final Element Leg 1-2: 254SV675, 254SV673 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV675, 254SV673.

Table 1076 Reliability Data Final Element Leg 1-2 254SV675, 254SV673

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Kvävgas till Vätgastank B (close)

The information and reliability data underneath describe the Kvävgas till Vätgastank B (close) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank B (close) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV674 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 254SV674

The following table shows the equipment that defines final element leg 1-1 254SV674.

Table 1077 Final Element Leg 1-1: 254SV674 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV674.

Table 1078 Reliability Data Final Element Leg 1-1 254SV674

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL) => Stop electrolyzer A

This chapter details the SIL Verification results, selections, and assumptions for the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Flow A (341FZ538 FZA LL) => Stop electrolyzer A |
| --- | --- |
| SIF Tag | SIF-094 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 152.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1079 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.57E-03 | 152.2 | 2 | 2 | N/A | 18.9 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1080 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.26E-04 | 2 | N/A | 202.31 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lutflöde A

The information and reliability data underneath describe the Lutflöde A sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lutflöde A |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341FZ538 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341FZ538

The following table shows the equipment that defines sensor leg 1-1 341FZ538.

Table 1081 Sensor Leg 1-1: 341FZ538 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Rota Yokogawa RAMC (standard limit switches) | 2014.Q2.04 | - | - | A | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341FZ538.

Table 1082 Reliability Data Sensor Leg 1-1 341FZ538

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Rota Yokogawa RAMC (standard limit switches) | - - | - - | - - | - - | 4.50E-08 4.50E-08 | 1.00E-08 1.00E-08 | 7.30E-08 7.30E-08 | - - | - - | 1.35E-07 1.35E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 87.8 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1083 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1084 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1085 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A Safety Instrumented Function is quantified as follows.

Table 1086 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1087 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1088 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL) => Stop electrolyzer B

This chapter details the SIL Verification results, selections, and assumptions for the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lye Flow B (341FZ578 FZA LL) => Stop electrolyzer B |
| --- | --- |
| SIF Tag | SIF-095 |
| SIF Description: | PSD needs to be constructed to have a safe shut-of for Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 152.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1089 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.57E-03 | 152.3 | 2 | 2 | N/A | 18.9 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1090 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.25E-04 | 2 | N/A | 202.31 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lutflöde B

The information and reliability data underneath describe the Lutflöde B sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lutflöde B |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | Sensor Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: Sensor Leg

The following table shows the equipment that defines sensor leg 1-1 Sensor Leg.

Table 1091 Sensor Leg 1-1: Sensor Leg Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Rota Yokogawa RAMC (standard limit switches) | 2014.Q2.04 | - | - | A | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 Sensor Leg.

Table 1092 Reliability Data Sensor Leg 1-1 Sensor Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Rota Yokogawa RAMC (standard limit switches) | - - | - - | - - | - - | 4.50E-08 4.50E-08 | 1.00E-08 1.00E-08 | 7.30E-08 7.30E-08 | - - | - - | 1.35E-07 1.35E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 87.8 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1093 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1094 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1095 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B Safety Instrumented Function is quantified as follows.

Table 1096 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1097 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1098 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2 Gasholder waterseal (341LZ365 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133 |
| --- | --- |
| SIF Tag | SIF-096 |
| SIF Description: | PSD needs to be constructed to have a safe shut of off Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 83.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1099 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.19E-02 | 83.7 | 1 | 2 | N/A | 19.78 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1100 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.85E-04 | 2 | N/A | 93.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: H2 Gasholder waterseal

The information and reliability data underneath describe the H2 Gasholder waterseal sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2 Gasholder waterseal |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LZ365 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LZ365

The following table shows the equipment that defines sensor leg 1-1 341LZ365.

Table 1101 Sensor Leg 1-1: 341LZ365 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LZ365.

Table 1102 Reliability Data Sensor Leg 1-1 341LZ365

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1103 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1104 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1105 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1106 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.16E-02 | 2 | N/A | 349.46 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1107 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1108 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1109 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1110 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1111 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1112 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1113 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1114 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Compressor Waterseal Level (341LZ366 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133 |
| --- | --- |
| SIF Tag | SIF-097 |
| SIF Description: | PSD needs to be constructed to have a safe shut of off Electrolyzer |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 83.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1115 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.19E-02 | 83.7 | 1 | 2 | N/A | 19.78 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1116 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.85E-04 | 2 | N/A | 93.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Compressor Waterseal Level

The information and reliability data underneath describe the Compressor Waterseal Level sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Compressor Waterseal Level |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LZ366 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LZ366

The following table shows the equipment that defines sensor leg 1-1 341LZ366.

Table 1117 Sensor Leg 1-1: 341LZ366 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LZ366.

Table 1118 Reliability Data Sensor Leg 1-1 341LZ366

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1119 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1120 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1121 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133 Safety Instrumented Function is quantified as follows.

Table 1122 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.16E-02 | 2 | N/A | 349.46 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1123 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1124 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1125 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1126 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1127 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1128 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1129 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1130 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H) => Stop Comp. A motor 341PU132

This chapter details the SIL Verification results, selections, and assumptions for the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. A Separator 1 level switch H (341LS428 LZA H) => Stop Comp. A motor 341PU132 |
| --- | --- |
| SIF Tag | SIF-098 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1203.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1131 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.31E-04 | 1203.7 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1132 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Separator 1 level switch H

The information and reliability data underneath describe the Comp. A Separator 1 level switch H sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Separator 1 level switch H |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS428 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS428

The following table shows the equipment that defines sensor leg 1-1 341LS428.

Table 1133 Sensor Leg 1-1: 341LS428 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS428.

Table 1134 Reliability Data Sensor Leg 1-1 341LS428

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1135 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1136 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1137 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1138 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1139 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1140 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132

This chapter details the SIL Verification results, selections, and assumptions for the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 |
| --- | --- |
| SIF Tag | SIF-099 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1203.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1141 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.31E-04 | 1203.7 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1142 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Separator 2 level switch H

The information and reliability data underneath describe the Comp. A Separator 2 level switch H sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Separator 2 level switch H |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS438 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS438

The following table shows the equipment that defines sensor leg 1-1 341LS438.

Table 1143 Sensor Leg 1-1: 341LS438 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS438.

Table 1144 Reliability Data Sensor Leg 1-1 341LS438

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1145 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1146 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1147 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1148 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1149 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1150 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL ) => Close 341SV926

This chapter details the SIL Verification results, selections, and assumptions for the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. A Condensate level switch LL (341LS449 LZA LL ) => Close 341SV926 |
| --- | --- |
| SIF Tag | SIF-100 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 112.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | Yes |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1151 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.91E-03 | 112.1 | 2 | 2 | N/A | 19.95 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function is quantified as follows.

Table 1152 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.24E-04 | 2 | N/A | 121.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Condensate level switch

The information and reliability data underneath describe the Comp. A Condensate level switch sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Condensate level switch |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS449 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS449

The following table shows the equipment that defines sensor leg 1-1 341LS449.

Table 1153 Sensor Leg 1-1: 341LS449 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS449.

Table 1154 Reliability Data Sensor Leg 1-1 341LS449

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function is quantified as follows.

Table 1155 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1156 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1157 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926 Safety Instrumented Function is quantified as follows.

Table 1158 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.09E-03 | 2 | N/A | 202.2 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close 341SV926

The information and reliability data underneath describe the Close 341SV926 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 341SV926 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV926 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 96 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV926

The following table shows the equipment that defines final element leg 1-1 341SV926.

Table 1159 Final Element Leg 1-1: 341SV926 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV926.

Table 1160 Reliability Data Final Element Leg 1-1 341SV926

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH) => Stop Comp. A motor 341PU132

This chapter details the SIL Verification results, selections, and assumptions for the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. A Outlet pressure transmitter (341PS442 PZA HH) => Stop Comp. A motor 341PU132 |
| --- | --- |
| SIF Tag | SIF-101 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 522.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1161 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.91E-03 | 522.9 | 2 | 2 | N/A | 20.04 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1162 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.75E-03 | 2 | N/A | 119.82 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Outlet pressure transmitter

The information and reliability data underneath describe the Comp. A Outlet pressure transmitter sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Outlet pressure transmitter |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PS442 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PS442

The following table shows the equipment that defines sensor leg 1-1 341PS442.

Table 1163 Sensor Leg 1-1: 341PS442 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar M - metal sensor | 2006.Q2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PS442.

Table 1164 Reliability Data Sensor Leg 1-1 341PS442

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar M - metal sensor | 1.32E-07 - | 4.63E-08 - | - - | - 1.78E-07 | - - | - - | 1.55E-07 1.55E-07 | - - | 2.12E-09 2.12E-09 | 2.08E-07 2.08E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 86.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1165 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1166 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1167 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1168 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1169 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1170 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132

This chapter details the SIL Verification results, selections, and assumptions for the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 |
| --- | --- |
| SIF Tag | SIF-102 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 522.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1171 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.91E-03 | 522.9 | 2 | 2 | N/A | 20.04 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1172 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.75E-03 | 2 | N/A | 119.82 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Inlet pressure transmitter

The information and reliability data underneath describe the Comp. A Inlet pressure transmitter sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Inlet pressure transmitter |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PS420 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PS420

The following table shows the equipment that defines sensor leg 1-1 341PS420.

Table 1173 Sensor Leg 1-1: 341PS420 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar M - metal sensor | 2006.Q2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PS420.

Table 1174 Reliability Data Sensor Leg 1-1 341PS420

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar M - metal sensor | 1.32E-07 - | 4.63E-08 - | - - | - 1.78E-07 | - - | - - | 1.55E-07 1.55E-07 | - - | 2.12E-09 2.12E-09 | 2.08E-07 2.08E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 86.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1175 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1176 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1177 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1178 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1179 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1180 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 |
| --- | --- |
| SIF Tag | SIF-104 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1203.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1181 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.31E-04 | 1203.7 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1182 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Separator 1 level switch

The information and reliability data underneath describe the Comp. B Separator 1 level switch sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Separator 1 level switch |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS468 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS468

The following table shows the equipment that defines sensor leg 1-1 341LS468.

Table 1183 Sensor Leg 1-1: 341LS468 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS468.

Table 1184 Reliability Data Sensor Leg 1-1 341LS468

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1185 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1186 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1187 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1188 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1189 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1190 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 |
| --- | --- |
| SIF Tag | SIF-105 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1203.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1191 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.31E-04 | 1203.7 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1192 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Separator 2 level switch

The information and reliability data underneath describe the Comp. B Separator 2 level switch sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Separator 2 level switch |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS478 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS478

The following table shows the equipment that defines sensor leg 1-1 341LS478.

Table 1193 Sensor Leg 1-1: 341LS478 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS478.

Table 1194 Reliability Data Sensor Leg 1-1 341LS478

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1195 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1196 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1197 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1198 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1199 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1200 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966

This chapter details the SIL Verification results, selections, and assumptions for the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 |
| --- | --- |
| SIF Tag | SIF-106 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 112.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1201 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.91E-03 | 112.1 | 2 | 2 | N/A | 19.95 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function is quantified as follows.

Table 1202 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.24E-04 | 2 | N/A | 121.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Condensate level switch LL

The information and reliability data underneath describe the Comp. B Condensate level switch LL sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Condensate level switch LL |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS489 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS489

The following table shows the equipment that defines sensor leg 1-1 341LS489.

Table 1203 Sensor Leg 1-1: 341LS489 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS489.

Table 1204 Reliability Data Sensor Leg 1-1 341LS489

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function is quantified as follows.

Table 1205 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1206 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1207 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 Safety Instrumented Function is quantified as follows.

Table 1208 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.09E-03 | 2 | N/A | 202.2 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close 341SV966

The information and reliability data underneath describe the Close 341SV966 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 341SV966 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV966 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 96 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV966

The following table shows the equipment that defines final element leg 1-1 341SV966.

Table 1209 Final Element Leg 1-1: 341SV966 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV966.

Table 1210 Reliability Data Final Element Leg 1-1 341SV966

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH) => Stop Comp. B motor 341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Comp. B Outlet pressure transmitter (341PS482 PZA HH) => Stop Comp. B motor 341PU133 |
| --- | --- |
| SIF Tag | SIF-107 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 522.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1211 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.91E-03 | 522.9 | 2 | 2 | N/A | 20.04 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1212 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.75E-03 | 2 | N/A | 119.82 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Outlet pressure transmitter

The information and reliability data underneath describe the Comp. B Outlet pressure transmitter sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Outlet pressure transmitter |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PS482 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PS482

The following table shows the equipment that defines sensor leg 1-1 341PS482.

Table 1213 Sensor Leg 1-1: 341PS482 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar M - metal sensor | 2006.Q2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PS482.

Table 1214 Reliability Data Sensor Leg 1-1 341PS482

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar M - metal sensor | 1.32E-07 - | 4.63E-08 - | - - | - 1.78E-07 | - - | - - | 1.55E-07 1.55E-07 | - - | 2.12E-09 2.12E-09 | 2.08E-07 2.08E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 86.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1215 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1216 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1217 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1218 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1219 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1220 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 |
| --- | --- |
| SIF Tag | SIF-108 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 522.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1221 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.91E-03 | 522.9 | 2 | 2 | N/A | 20.04 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1222 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.75E-03 | 2 | N/A | 119.82 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Inlet pressure transmitter

The information and reliability data underneath describe the Comp. B Inlet pressure transmitter sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Inlet pressure transmitter |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PS460 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PS460

The following table shows the equipment that defines sensor leg 1-1 341PS460.

Table 1223 Sensor Leg 1-1: 341PS460 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar M - metal sensor | 2006.Q2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PS460.

Table 1224 Reliability Data Sensor Leg 1-1 341PS460

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar M - metal sensor | 1.32E-07 - | 4.63E-08 - | - - | - 1.78E-07 | - - | - - | 1.55E-07 1.55E-07 | - - | 2.12E-09 2.12E-09 | 2.08E-07 2.08E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 86.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1225 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1226 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1227 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1228 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.57E-04 | 2 | N/A | 218.29 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 24 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1229 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1230 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999

This chapter details the SIL Verification results, selections, and assumptions for the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 |
| --- | --- |
| SIF Tag | SIF-110 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 112.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1231 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.91E-03 | 112.1 | 2 | 2 | N/A | 19.95 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function is quantified as follows.

Table 1232 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.24E-04 | 2 | N/A | 121.88 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Dryer drain level switch

The information and reliability data underneath describe the Dryer drain level switch sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Dryer drain level switch |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LZ499 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LZ499

The following table shows the equipment that defines sensor leg 1-1 341LZ499.

Table 1233 Sensor Leg 1-1: 341LZ499 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LZ499.

Table 1234 Reliability Data Sensor Leg 1-1 341LZ499

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function is quantified as follows.

Table 1235 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1236 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1237 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 Safety Instrumented Function is quantified as follows.

Table 1238 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.09E-03 | 2 | N/A | 202.2 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close 341SV999

The information and reliability data underneath describe the Close 341SV999 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 341SV999 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV999 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 96 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV999

The following table shows the equipment that defines final element leg 1-1 341SV999.

Table 1239 Final Element Leg 1-1: 341SV999 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV999.

Table 1240 Reliability Data Final Element Leg 1-1 341SV999

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H) => Stop Comp. A motor 341PU132

This chapter details the SIL Verification results, selections, and assumptions for the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. A Inlet filter level switch H (341LS423 LZA H) => Stop Comp. A motor 341PU132 |
| --- | --- |
| SIF Tag | SIF-111 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1306.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1241 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.65E-04 | 1306.5 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1242 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. A Separator 1 level switch H

The information and reliability data underneath describe the Comp. A Separator 1 level switch H sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. A Separator 1 level switch H |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS423 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS423

The following table shows the equipment that defines sensor leg 1-1 341LS423.

Table 1243 Sensor Leg 1-1: 341LS423 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS423.

Table 1244 Reliability Data Sensor Leg 1-1 341LS423

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1245 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1246 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1247 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132 Safety Instrumented Function is quantified as follows.

Table 1248 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.14E-05 | 2 | N/A | 218.28 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. A motor

The information and reliability data underneath describe the Trip Comp. A motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. A motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU132 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU132

The following table shows the equipment that defines final element leg 1-1 341PU132.

Table 1249 Final Element Leg 1-1: 341PU132 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU132.

Table 1250 Reliability Data Final Element Leg 1-1 341PU132

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133

This chapter details the SIL Verification results, selections, and assumptions for the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 |
| --- | --- |
| SIF Tag | SIF-112 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1306.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1251 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.65E-04 | 1306.5 | 3 | 2 | N/A | 20.05 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1252 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.71E-04 | 2 | N/A | 120.06 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Comp. B Separator 1 level switch

The information and reliability data underneath describe the Comp. B Separator 1 level switch sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Comp. B Separator 1 level switch |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341LS463 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341LS463

The following table shows the equipment that defines sensor leg 1-1 341LS463.

Table 1253 Sensor Leg 1-1: 341LS463 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341LS463.

Table 1254 Reliability Data Sensor Leg 1-1 341LS463

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1255 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1256 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1257 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 Safety Instrumented Function is quantified as follows.

Table 1258 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.14E-05 | 2 | N/A | 218.28 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Trip Comp. B motor

The information and reliability data underneath describe the Trip Comp. B motor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip Comp. B motor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341PU133 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341PU133

The following table shows the equipment that defines final element leg 1-1 341PU133.

Table 1259 Final Element Leg 1-1: 341PU133 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341PU133.

Table 1260 Reliability Data Final Element Leg 1-1 341PU133

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence) => Stop electrolyzer A+B (prevent start) SIL2 | Pressure after dryer (341PZ371 L2) => Stop electrolyzer A+B (prevent start)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence) => Stop electrolyzer A+B (prevent start) SIL2 ¦ Pressure after dryer (341PZ371 L2) => Stop electrolyzer A+B (prevent start) |
| --- | --- |
| SIF Tag | SIF-113 |
| SIF Description: | For full description of this function, see functional description. This is a verification that the nitrogen flushing sequence to prevent air being left in system has been succesful. Lowlow-trip prevents to start a depressurized unit without running nitrogen flushing sequence. A depressurized unit could potentially lead to air ingress to unit. |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 117.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1261 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.50E-03 | 117.5 | 2 | 2 | N/A | 22.17 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function is quantified as follows.

Table 1262 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.35E-04 | 2 | N/A | 1254.3 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Pressure after dryer

The information and reliability data underneath describe the Pressure after dryer sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Pressure after dryer |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PZ371 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PZ371

The following table shows the equipment that defines sensor leg 1-1 341PZ371.

Table 1263 Sensor Leg 1-1: 341PZ371 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Wika IS-3 |  | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PZ371.

Table 1264 Reliability Data Sensor Leg 1-1 341PZ371

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Wika IS-3 | - - | - - | - - | - - | 9.10E-08 9.10E-08 | - - | 4.00E-08 4.00E-08 | - - | - - | - - |
|  |  |  |  |  |  |  | SFF [%] |  |  | 69.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function is quantified as follows.

Table 1265 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1266 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1267 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start) Safety Instrumented Function is quantified as follows.

Table 1268 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.27E-03 | 2 | N/A | 136.23 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Main circuit breaker A

The information and reliability data underneath describe the Main circuit breaker A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Main circuit breaker A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1269 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1270 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Main circuit breaker B

The information and reliability data underneath describe the Main circuit breaker B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Main circuit breaker B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1271 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1272 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240

This chapter details the SIL Verification results, selections, and assumptions for the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 354TI442 => stop heater 354HE240 |
| --- | --- |
| SIF Tag | SIF-114 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 75.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1273 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.32E-02 | 75.7 | 1 | 2 | N/A | 16.07 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1274 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 354TI442

The information and reliability data underneath describe the High temperature Kanthal 354TI442 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 354TI442 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI442 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354TI442

The following table shows the equipment that defines sensor leg 1-1 354TI442.

Table 1275 Sensor Leg 1-1: 354TI442 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354TI442.

Table 1276 Reliability Data Sensor Leg 1-1 354TI442

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1277 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1278 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1279 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1280 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE240

The information and reliability data underneath describe the Stop heater 354HE240 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE240 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1281 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1282 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240

This chapter details the SIL Verification results, selections, and assumptions for the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 354TI443 => stop heater 354HE240 |
| --- | --- |
| SIF Tag | SIF-115 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 75.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1283 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.32E-02 | 75.7 | 1 | 2 | N/A | 16.07 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1284 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 354TI443

The information and reliability data underneath describe the High temperature Kanthal 354TI443 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 354TI443 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI443 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354TI443

The following table shows the equipment that defines sensor leg 1-1 354TI443.

Table 1285 Sensor Leg 1-1: 354TI443 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354TI443.

Table 1286 Reliability Data Sensor Leg 1-1 354TI443

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1287 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1288 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1289 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1290 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE240

The information and reliability data underneath describe the Stop heater 354HE240 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE240 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1291 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1292 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240

This chapter details the SIL Verification results, selections, and assumptions for the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 354TI444 => stop heater 354HE240 |
| --- | --- |
| SIF Tag | SIF-116 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 75.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1293 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.32E-02 | 75.7 | 1 | 2 | N/A | 16.07 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1294 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 354TI444

The information and reliability data underneath describe the High temperature Kanthal 354TI444 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 354TI444 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI444 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354TI444

The following table shows the equipment that defines sensor leg 1-1 354TI444.

Table 1295 Sensor Leg 1-1: 354TI444 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354TI444.

Table 1296 Reliability Data Sensor Leg 1-1 354TI444

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1297 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1298 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1299 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240 Safety Instrumented Function is quantified as follows.

Table 1300 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE240

The information and reliability data underneath describe the Stop heater 354HE240 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE240 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1301 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1302 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Temp kondensor processgas (321XI319¦H2) |
| --- | --- |
| SIF Tag | SIF-117 |
| SIF Description: | SIL1 Temp kondensor processgas (321TI320, 321TI321, 321TI322¦H2) => Trip Processgaskompressor (354PU101 SIL2) Close NG till kylkrets (252SV614 SIL2) Close H2 till uppkolningskrets (341SV881) Close CO till uppkolningskrets (356SV511) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 88.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1303 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.13E-02 | 88.4 | 1 | 2 | N/A | 24.25 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function is quantified as follows.

Table 1304 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.32E-04 | 3 | N/A | 585.39 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temp kondensor processgas

The information and reliability data underneath describe the Temp kondensor processgas sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temp kondensor processgas |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 321TI320, 321TI321, 321TI322 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 321TI320, 321TI321, 321TI322

The following table shows the equipment that defines sensor leg 1-3 321TI320, 321TI321, 321TI322.

Table 1305 Sensor Leg 1-3: 321TI320, 321TI321, 321TI322 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 321TI320, 321TI321, 321TI322.

Table 1306 Reliability Data Sensor Leg 1-3 321TI320, 321TI321, 321TI322

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function is quantified as follows.

Table 1307 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1308 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1309 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2) Safety Instrumented Function is quantified as follows.

Table 1310 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.12E-02 | 2 | N/A | 391.09 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Trip proc.gaskompressor

The information and reliability data underneath describe the Trip proc.gaskompressor final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Trip proc.gaskompressor |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 1311 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 1312 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close NG till kylkrets

The information and reliability data underneath describe the Close NG till kylkrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close NG till kylkrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV614 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 97 |
| Proof Test Execution: | Offline |
| Partial Valve Stroke Test Interval | 6M |
| Partial Valve Stroke Test Coverage[%] | 77 |
| Partial Valve Stroke Test Execution | Manual |

##### Final Element Leg 1-1: 252SV614

The following table shows the equipment that defines final element leg 1-1 252SV614.

Table 1313 Final Element Leg 1-1: 252SV614 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 252SV614.

Table 1314 Reliability Data Final Element Leg 1-1 252SV614

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - 5.70E-08 | 5.70E-08 - | - 5.07E-07 | 6.54E-07 1.47E-07 | - | - | - |
| Rotork | - - | - - | - - | 3.15E-08 4.25E-09 | - | - | - |
| Transworld Mars | - - | - - | - - | 3.73E-07 - | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Close H2 till uppkolningskrets

The information and reliability data underneath describe the Close H2 till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close H2 till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV881 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV881

The following table shows the equipment that defines final element leg 1-1 341SV881.

Table 1315 Final Element Leg 1-1: 341SV881 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV881.

Table 1316 Reliability Data Final Element Leg 1-1 341SV881

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: Close CO till uppkolningskrets

The information and reliability data underneath describe the Close CO till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close CO till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV511 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 356SV511

The following table shows the equipment that defines final element leg 1-1 356SV511.

Table 1317 Final Element Leg 1-1: 356SV511 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 356SV511.

Table 1318 Reliability Data Final Element Leg 1-1 356SV511

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230

This chapter details the SIL Verification results, selections, and assumptions for the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 |
| --- | --- |
| SIF Tag | SIF-118 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 78.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1319 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.27E-02 | 78.6 | 1 | 2 | N/A | 13.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1320 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.86E-04 | 3 | N/A | 56.31 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Chromalox 354TI331 and 354TI332

The information and reliability data underneath describe the High temperature Chromalox 354TI331 and 354TI332 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Chromalox 354TI331 and 354TI332 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI331, 354TI332 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 354TI331, 354TI332

The following table shows the equipment that defines sensor leg 1-2 354TI331, 354TI332.

Table 1321 Sensor Leg 1-2: 354TI331, 354TI332 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| PR Electronics 9116-1-V2R0, current in and out | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 354TI331, 354TI332.

Table 1322 Reliability Data Sensor Leg 1-2 354TI331, 354TI332

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| PR Electronics 9116-1-V2R0, current in and out | 2.07E-07 - | 5.00E-09 - | 3.17E-07 - | - - | - 3.22E-07 | - - | 4.10E-08 2.48E-07 | 2.50E-08 2.50E-08 | 1.00E-09 1.00E-09 | 4.44E-07 4.44E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 82.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1323 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1324 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1325 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1326 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE230

The information and reliability data underneath describe the Stop heater 354HE230 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE230 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1327 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1328 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230

This chapter details the SIL Verification results, selections, and assumptions for the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 |
| --- | --- |
| SIF Tag | SIF-119 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 78.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1329 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.27E-02 | 78.6 | 1 | 2 | N/A | 13.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1330 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.86E-04 | 3 | N/A | 56.31 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Chromalox 354TI335 and 354TI336

The information and reliability data underneath describe the High temperature Chromalox 354TI335 and 354TI336 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Chromalox 354TI335 and 354TI336 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI335, 354TI336 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 354TI335, 354TI336

The following table shows the equipment that defines sensor leg 1-2 354TI335, 354TI336.

Table 1331 Sensor Leg 1-2: 354TI335, 354TI336 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| PR Electronics 9116-1-V2R0, current in and out | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 354TI335, 354TI336.

Table 1332 Reliability Data Sensor Leg 1-2 354TI335, 354TI336

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| PR Electronics 9116-1-V2R0, current in and out | 2.07E-07 - | 5.00E-09 - | 3.17E-07 - | - - | - 3.22E-07 | - - | 4.10E-08 2.48E-07 | 2.50E-08 2.50E-08 | 1.00E-09 1.00E-09 | 4.44E-07 4.44E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 82.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1333 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1334 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1335 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1336 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE230

The information and reliability data underneath describe the Stop heater 354HE230 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE230 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1337 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1338 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230

This chapter details the SIL Verification results, selections, and assumptions for the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 |
| --- | --- |
| SIF Tag | SIF-120 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 78.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1339 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.27E-02 | 78.6 | 1 | 2 | N/A | 13.62 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1340 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.86E-04 | 3 | N/A | 56.31 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Chromalox 354TI339 and 354TI340

The information and reliability data underneath describe the High temperature Chromalox 354TI339 and 354TI340 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Chromalox 354TI339 and 354TI340 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI339, 354TI340 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 354TI339, 354TI340

The following table shows the equipment that defines sensor leg 1-2 354TI339, 354TI340.

Table 1341 Sensor Leg 1-2: 354TI339, 354TI340 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| PR Electronics 9116-1-V2R0, current in and out | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 354TI339, 354TI340.

Table 1342 Reliability Data Sensor Leg 1-2 354TI339, 354TI340

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| PR Electronics 9116-1-V2R0, current in and out | 2.07E-07 - | 5.00E-09 - | 3.17E-07 - | - - | - 3.22E-07 | - - | 4.10E-08 2.48E-07 | 2.50E-08 2.50E-08 | 1.00E-09 1.00E-09 | 4.44E-07 4.44E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 82.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1343 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1344 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1345 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 Safety Instrumented Function is quantified as follows.

Table 1346 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.23E-02 | 2 | N/A | 53.46 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 354HE230

The information and reliability data underneath describe the Stop heater 354HE230 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 354HE230 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354HE240 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354HE240

The following table shows the equipment that defines final element leg 1-1 354HE240.

Table 1347 Final Element Leg 1-1: 354HE240 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Generic Relay | 2006.2.02 | - | - | A | - |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354HE240.

Table 1348 Reliability Data Final Element Leg 1-1 354HE240

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Generic Relay | - | 9.00E-07 | - | 6.00E-07 | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 70.4 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦H2) |
| --- | --- |
| SIF Tag | SIF-121 |
| SIF Description: | OBS notera att samtliga slutdon inte är angivna i denna. Se SIF-11 356SV511 341SV881 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 132.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1349 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.56E-03 | 132.1 | 2 | 2 | N/A | 23.94 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function is quantified as follows.

Table 1350 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.17E-05 | 3 | N/A | 2036.08 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 321YM014 H2

The information and reliability data underneath describe the 321YM014 H2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 321YM014 H2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 321PI315, 321PI316, 321PI317 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 321PI315, 321PI316, 321PI317

The following table shows the equipment that defines sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1351 Sensor Leg 1-3: 321PI315, 321PI316, 321PI317 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | On |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1352 Reliability Data Sensor Leg 1-3 321PI315, 321PI316, 321PI317

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - 4.48E-07 | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function is quantified as follows.

Table 1353 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1354 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1355 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2) Safety Instrumented Function is quantified as follows.

Table 1356 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.50E-03 | 2 | N/A | 231.72 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Final Element Group 1: Close H2 till uppkolningskrets

The information and reliability data underneath describe the Close H2 till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close H2 till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV881 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV881

The following table shows the equipment that defines final element leg 1-1 341SV881.

Table 1357 Final Element Leg 1-1: 341SV881 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV881.

Table 1358 Reliability Data Final Element Leg 1-1 341SV881

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close CO till uppkolningskrets

The information and reliability data underneath describe the Close CO till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close CO till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV511 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 356SV511

The following table shows the equipment that defines final element leg 1-1 356SV511.

Table 1359 Final Element Leg 1-1: 356SV511 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 356SV511.

Table 1360 Reliability Data Final Element Leg 1-1 356SV511

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦L2) |
| --- | --- |
| SIF Tag | SIF-122 |
| SIF Description: | OBS notera att samtliga slutdon inte är angivna i denna. Se SIF-12 356SV511 341SV881 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 130.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1361 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.64E-03 | 130.9 | 2 | 2 | N/A | 24.01 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function is quantified as follows.

Table 1362 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.17E-05 | 3 | N/A | 2036.08 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 321YM014 L2

The information and reliability data underneath describe the 321YM014 L2 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 321YM014 L2 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 321PI315, 321PI316, 321PI317 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 321PI315, 321PI316, 321PI317

The following table shows the equipment that defines sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1363 Sensor Leg 1-3: 321PI315, 321PI316, 321PI317 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | On |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1364 Reliability Data Sensor Leg 1-3 321PI315, 321PI316, 321PI317

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - 4.48E-07 | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function is quantified as follows.

Table 1365 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1366 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1367 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2) Safety Instrumented Function is quantified as follows.

Table 1368 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.57E-03 | 2 | N/A | 238.57 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: Close H2 till uppkolningskrets

The information and reliability data underneath describe the Close H2 till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close H2 till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV881 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV881

The following table shows the equipment that defines final element leg 1-1 341SV881.

Table 1369 Final Element Leg 1-1: 341SV881 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV881.

Table 1370 Reliability Data Final Element Leg 1-1 341SV881

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close CO till uppkolningskrets

The information and reliability data underneath describe the Close CO till uppkolningskrets final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close CO till uppkolningskrets |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV511 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 356SV511

The following table shows the equipment that defines final element leg 1-1 356SV511.

Table 1371 Final Element Leg 1-1: 356SV511 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 356SV511.

Table 1372 Reliability Data Final Element Leg 1-1 356SV511

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦H3) |
| --- | --- |
| SIF Tag | SIF-123 |
| SIF Description: | Gastryck toppgas (321PI315, 321PI316 & 321PI317¦H3) => Open nödventil eft. spraykylare (345SV524 & 353SV524) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 112.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1373 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.89E-03 | 112.5 | 2 | 2 | N/A | 51.4 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function is quantified as follows.

Table 1374 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.20E-05 | 3 | N/A | 3972.77 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 321YM014 H3

The information and reliability data underneath describe the 321YM014 H3 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 321YM014 H3 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 321PI315, 321PI316, 321PI317 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 321PI315, 321PI316, 321PI317

The following table shows the equipment that defines sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1375 Sensor Leg 1-3: 321PI315, 321PI316, 321PI317 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | On |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1376 Reliability Data Sensor Leg 1-3 321PI315, 321PI316, 321PI317

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - 4.48E-07 | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function is quantified as follows.

Table 1377 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.62E-06 | 2 | N/A | 52.78 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 1378 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1379 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3) Safety Instrumented Function is quantified as follows.

Table 1380 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.85E-03 | 2 | N/A | 3915.32 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Open Topptryck nödventil eft. spraykylare red. gas

The information and reliability data underneath describe the Open Topptryck nödventil eft. spraykylare red. gas final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open Topptryck nödventil eft. spraykylare red. gas |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV524, 353SV524 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 345SV524, 353SV524

The following table shows the equipment that defines final element leg 1-2 345SV524, 353SV524.

Table 1381 Final Element Leg 1-2: 345SV524, 353SV524 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| GEFA HG1 |  | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 345SV524, 353SV524.

Table 1382 Reliability Data Final Element Leg 1-2 345SV524, 353SV524

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| GEFA HG1 | - | - | - | 1.56E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 55.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging

This chapter details the SIL Verification results, selections, and assumptions for the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging |
| --- | --- |
| SIF Tag | SIF-124 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 34.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1383 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.86E-02 | 34.9 | 1 | 2 | N/A | 23.76 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1384 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.18E-03 | 2 | N/A | 219.04 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low flow to O2 in H2 A Analyzer

The information and reliability data underneath describe the Low flow to O2 in H2 A Analyzer sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low flow to O2 in H2 A Analyzer |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341FS315 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341FS315

The following table shows the equipment that defines sensor leg 1-1 341FS315.

Table 1385 Sensor Leg 1-1: 341FS315 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Rota Yokogawa RAGK/RAGL, low current | 2011.Q4.03 | - | - | A | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341FS315.

Table 1386 Reliability Data Sensor Leg 1-1 341FS315

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Rota Yokogawa RAGK/RAGL, low current | - - | - - | - - | - - | 2.00E-09 2.00E-09 | 1.10E-08 1.10E-08 | 1.13E-07 1.13E-07 | - - | - - | 1.15E-07 1.15E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.3 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1387 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1388 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1389 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1390 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.74E-02 | 2 | N/A | 1843.7 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: Kvävgas till Vätgastank A (open)

The information and reliability data underneath describe the Kvävgas till Vätgastank A (open) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank A (open) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV665, 254SV663 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV665, 254SV663

The following table shows the equipment that defines final element leg 1-2 254SV665, 254SV663.

Table 1391 Final Element Leg 1-2: 254SV665, 254SV663 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV665, 254SV663.

Table 1392 Reliability Data Final Element Leg 1-2 254SV665, 254SV663

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Kvävgas till Vätgastank A (close)

The information and reliability data underneath describe the Kvävgas till Vätgastank A (close) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank A (close) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV664 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 254SV664

The following table shows the equipment that defines final element leg 1-1 254SV664.

Table 1393 Final Element Leg 1-1: 254SV664 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV664.

Table 1394 Reliability Data Final Element Leg 1-1 254SV664

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: PSD A

The information and reliability data underneath describe the PSD A final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD A |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1395 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1396 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging

This chapter details the SIL Verification results, selections, and assumptions for the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging |
| --- | --- |
| SIF Tag | SIF-125 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 34.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1397 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.86E-02 | 34.9 | 1 | 2 | N/A | 23.76 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1398 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.18E-03 | 2 | N/A | 219.04 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Low flow to O2 in H2 B Analyzer

The information and reliability data underneath describe the Low flow to O2 in H2 B Analyzer sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Low flow to O2 in H2 B Analyzer |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341FS335 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341FS335

The following table shows the equipment that defines sensor leg 1-1 341FS335.

Table 1399 Sensor Leg 1-1: 341FS335 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Rota Yokogawa RAGK/RAGL, low current | 2011.Q4.03 | - | - | A | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341FS335.

Table 1400 Reliability Data Sensor Leg 1-1 341FS335

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Rota Yokogawa RAGK/RAGL, low current | - - | - - | - - | - - | 2.00E-09 2.00E-09 | 1.10E-08 1.10E-08 | 1.13E-07 1.13E-07 | - - | - - | 1.15E-07 1.15E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 1.46E-07 | - - | 4.10E-08 6.80E-08 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 84.3 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1401 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1402 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1403 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging Safety Instrumented Function is quantified as follows.

Table 1404 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.74E-02 | 2 | N/A | 1843.7 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: PSD B

The information and reliability data underneath describe the PSD B final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | PSD B |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1405 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1406 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Kvävgas till Vätgastank B (open)

The information and reliability data underneath describe the Kvävgas till Vätgastank B (open) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank B (open) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV675, 254SV673 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 254SV675, 254SV673

The following table shows the equipment that defines final element leg 1-2 254SV675, 254SV673.

Table 1407 Final Element Leg 1-2: 254SV675, 254SV673 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 254SV675, 254SV673.

Table 1408 Reliability Data Final Element Leg 1-2 254SV675, 254SV673

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Kvävgas till Vätgastank B (close)

The information and reliability data underneath describe the Kvävgas till Vätgastank B (close) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Kvävgas till Vätgastank B (close) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 254SV674 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 254SV674

The following table shows the equipment that defines final element leg 1-1 254SV674.

Table 1409 Final Element Leg 1-1: 254SV674 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Bürkert Werke 3/2 way 6014-C-*** | 2006.Q2.02 | - | - | A | - |
| Bürkert Werke 2000-A-***/2002-A-*** | 2006.Q2.02 | - | - | A | - |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 254SV674.

Table 1410 Reliability Data Final Element Leg 1-1 254SV674

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Bürkert Werke 3/2 way 6014-C-*** | - | 8.60E-08 | - | 6.29E-08 | - | - | 8.95E-08 |
| Bürkert Werke 2000-A-***/2002-A-*** | - | 2.16E-08 | - | 2.26E-07 | - | - | 5.37E-07 |
|  |  |  |  |  | SFF [%] |  | 78.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH) => Stop heater 341HE266

This chapter details the SIL Verification results, selections, and assumptions for the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Dryer heater outlet temperature transmitter (341TI341 TZA HH) => Stop heater 341HE266 |
| --- | --- |
| SIF Tag | SIF-126 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 223.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1411 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.48E-03 | 223.4 | 2 | 2 | N/A | 19.45 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function is quantified as follows.

Table 1412 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.30E-04 | 2 | N/A | 292.22 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Dryer heater outlet temperature transmitter HH

The information and reliability data underneath describe the Dryer heater outlet temperature transmitter HH sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Dryer heater outlet temperature transmitter HH |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341TI341 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341TI341

The following table shows the equipment that defines sensor leg 1-1 341TI341.

Table 1413 Sensor Leg 1-1: 341TI341 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341TI341.

Table 1414 Reliability Data Sensor Leg 1-1 341TI341

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - 1.70E-08 | - - | - 4.07E-07 | 2.70E-08 2.70E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 97.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function is quantified as follows.

Table 1415 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1416 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1417 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266 Safety Instrumented Function is quantified as follows.

Table 1418 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.14E-03 | 2 | N/A | 90.82 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop heater 341HE266

The information and reliability data underneath describe the Stop heater 341HE266 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop heater 341HE266 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1419 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1420 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-127 SIL2 Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) |
| --- | --- |
| SIF Tag | SIF-127 |
| SIF Description: | SIL2 Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) ) => Close Avstängning tillopp spolvatten (345SV635) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 134.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1421 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.41E-03 | 134.9 | 2 | 2 | N/A | 16.56 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function is quantified as follows.

Table 1422 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.77E-04 | 3 | N/A | 1785.73 | 1 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: Tryckmätare hydrofor

The information and reliability data underneath describe the Tryckmätare hydrofor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckmätare hydrofor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 345PI420, 345PI421 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 345PI420, 345PI421

The following table shows the equipment that defines sensor leg 1-2 345PI420, 345PI421.

Table 1423 Sensor Leg 1-2: 345PI420, 345PI421 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 345PI420, 345PI421.

Table 1424 Reliability Data Sensor Leg 1-2 345PI420, 345PI421

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Tryckmätare hydrofor

The information and reliability data underneath describe the Tryckmätare hydrofor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryckmätare hydrofor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 321PI315, 321PI316, 321PI317 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 321PI315, 321PI316, 321PI317

The following table shows the equipment that defines sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1425 Sensor Leg 1-3: 321PI315, 321PI316, 321PI317 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 321PI315, 321PI316, 321PI317.

Table 1426 Reliability Data Sensor Leg 1-3 321PI315, 321PI316, 321PI317

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 78.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function is quantified as follows.

Table 1427 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.40E-06 | 2 | N/A | 17.12 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1428 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1429 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) Safety Instrumented Function is quantified as follows.

Table 1430 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.22E-03 | 2 | N/A | 709.66 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängning tillopp spolvatten

The information and reliability data underneath describe the Close Avstängning tillopp spolvatten final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängning tillopp spolvatten |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 345SV635 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 345SV635

The following table shows the equipment that defines final element leg 1-1 345SV635.

Table 1431 Final Element Leg 1-1: 345SV635 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Sirca AP-APM |  | - | - | A | 3 |
| Flowserve Worcester Series 44/59/459/599 | 2013.3.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 345SV635.

Table 1432 Reliability Data Final Element Leg 1-1 345SV635

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Sirca AP-APM | 3.00E-10 | 3.32E-10 | - | 3.48E-10 | - | - | - |
| Flowserve Worcester Series 44/59/459/599 | - | - | - | 4.68E-07 | - | - | 8.80E-07 |
|  |  |  |  |  | SFF [%] |  | 12.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Difftryck, H2 – Processgas 354XI327¦L2 (341PI882 - 354PI326) |
| --- | --- |
| SIF Tag | SIF-128 |
| SIF Description: | Difftryck, H2 – Processgas 354XI327¦L2 (341PI882 - 354PI326) => Close Avstängningsventil H2 till processgas. (341SV881 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 67.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1433 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.48E-02 | 67.5 | 1 | 2 | N/A | 18.91 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1434 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.03E-03 | 2 | N/A | 268851.38 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 341XI327

The information and reliability data underneath describe the 341XI327 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 341XI327 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PI882, 354PI326 |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95.9 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1: 341PI882

The following table shows the equipment that defines sensor leg 1 341PI882.

Table 1435 Sensor Leg 1: 341PI882 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exd | 2006.Q2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 341PI882.

Table 1436 Reliability Data Sensor Leg 1 341PI882

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exd | 5.21E-08 - | 8.75E-08 - | 3.55E-07 - | - - | - - | - - | 8.45E-08 5.79E-07 | - - | 1.00E-08 1.00E-08 | 4.40E-07 4.40E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 5.3 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 354PI326

The following table shows the equipment that defines sensor leg 2 354PI326.

Table 1437 Sensor Leg 2: 354PI326 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | None |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 354PI326.

Table 1438 Reliability Data Sensor Leg 2 354PI326

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - - | - - | 6.53E-08 5.13E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 6.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1439 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1440 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1441 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1442 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.82E-03 | 2 | N/A | 712.14 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängningsventil H2 till processgas. (341SV881 SIL2)

The information and reliability data underneath describe the Close Avstängningsventil H2 till processgas. (341SV881 SIL2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängningsventil H2 till processgas. (341SV881 SIL2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV881 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV881

The following table shows the equipment that defines final element leg 1-1 341SV881.

Table 1443 Final Element Leg 1-1: 341SV881 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV881.

Table 1444 Reliability Data Final Element Leg 1-1 341SV881

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Difftryck, CO – Processgas 354XI328¦L2 (356PI311 - 354PI326) |
| --- | --- |
| SIF Tag | SIF-129 |
| SIF Description: | SIL1 ¦ Difftryck, CO – Processgas 354XI328¦L2 (356PI311 - 354PI326) => Close Avstängningsventil CO till processgas. (356SV511 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 88 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1445 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.14E-02 | 88 | 1 | 2 | N/A | 18.89 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1446 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.40E-03 | 2 | N/A | 19570.98 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 354XI328

The information and reliability data underneath describe the 354XI328 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 354XI328 |
| --- | --- |
| Group Description: | 356PI311 - 354PI326 (L2=0,5barG) |
| Sensor Legs: | 356PI311, 354PI326 |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1: 356PI311

The following table shows the equipment that defines sensor leg 1 356PI311.

Table 1447 Sensor Leg 1: 356PI311 Details

| Sensor Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1 356PI311.

Table 1448 Reliability Data Sensor Leg 1 356PI311

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.79E-07 | - - | 6.53E-08 1.34E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 75.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

##### Sensor Leg 2: 354PI326

The following table shows the equipment that defines sensor leg 2 354PI326.

Table 1449 Sensor Leg 2: 354PI326 Details

| Sensor Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 2 354PI326.

Table 1450 Reliability Data Sensor Leg 2 354PI326

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 5.21E-08 | - - | 6.53E-08 4.61E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 15.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1451 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1452 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1453 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326) Safety Instrumented Function is quantified as follows.

Table 1454 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.98E-03 | 2 | N/A | 712.98 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close Avstängningsventil CO till processgas. (356SV511 SIL2)

The information and reliability data underneath describe the Close Avstängningsventil CO till processgas. (356SV511 SIL2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close Avstängningsventil CO till processgas. (356SV511 SIL2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV511 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 356SV511

The following table shows the equipment that defines final element leg 1-1 356SV511.

Table 1455 Final Element Leg 1-1: 356SV511 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 356SV511.

Table 1456 Reliability Data Final Element Leg 1-1 356SV511

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 11.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5))

This chapter details the SIL Verification results, selections, and assumptions for the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Difftryck H2-linje till red.krets 343XI308¦L2 (341PI675<(343PZ305/7/8+0,5)) |
| --- | --- |
| SIF Tag | SIF-130 |
| SIF Description: | SIL1 ¦ Difftryck H2-linje till red.krets (Skydd backfl.343XI308) (341PI675<(343PZ305/7/8+0,5)) => close 341SV672 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 102.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1457 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 9.79E-03 | 102.1 | 2 | 2 | N/A | 18.89 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1458 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.98E-03 | 2 | N/A | 13531.06 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: 343XI308|L2 (341PI675)

The information and reliability data underneath describe the 343XI308|L2 (341PI675) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 343XI308¦L2 (341PI675) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PI675 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PI675

The following table shows the equipment that defines sensor leg 1-1 341PI675.

Table 1459 Sensor Leg 1-1: 341PI675 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PI675.

Table 1460 Reliability Data Sensor Leg 1-1 341PI675

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.53E-08 4.44E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: 343XI308|L2 (343PZ305+0,5)

The information and reliability data underneath describe the 343XI308|L2 (343PZ305+0,5) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 343XI308¦L2 (343PZ305+0,5) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PZ305, 343PZ307, 343PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308

The following table shows the equipment that defines sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 1461 Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 1462 Reliability Data Sensor Leg 1-3 343PZ305, 343PZ307, 343PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 5.21E-08 | - - | 8.00E-08 4.47E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 15.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1463 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1464 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1465 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1466 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.82E-03 | 2 | N/A | 712.14 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 341SV672

The information and reliability data underneath describe the close 341SV672 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 341SV672 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV672 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV672

The following table shows the equipment that defines final element leg 1-1 341SV672.

Table 1467 Final Element Leg 1-1: 341SV672 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV672.

Table 1468 Reliability Data Final Element Leg 1-1 341SV672

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5))

This chapter details the SIL Verification results, selections, and assumptions for the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Difftryck NG-linje till red.krets 343XI307¦L2 (252PI565<(343PZ305/7/8+0,5)) |
| --- | --- |
| SIF Tag | SIF-131 |
| SIF Description: | SIL1 ¦ Difftryck NG-linje till red.krets 343XI307¦L2 (252PI565<(343PZ305/7/8+0,5)) => Close 252SV562 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 196.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1469 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.09E-03 | 196.5 | 2 | 2 | N/A | 36.85 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1470 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.56E-03 | 2 | N/A | 26399.15 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: | 10 |

#### Sensor Group 1: 343XI307|L2  (252PI565)

The information and reliability data underneath describe the 343XI307|L2  (252PI565) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 343XI307¦L2 (252PI565) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 252PI565 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-1: 252PI565

The following table shows the equipment that defines sensor leg 1-1 252PI565.

Table 1471 Sensor Leg 1-1: 252PI565 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 252PI565.

Table 1472 Reliability Data Sensor Leg 1-1 252PI565

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 6.85E-08 | - - | 6.89E-08 4.48E-07 | - - | 1.00E-08 1.00E-08 | 4.30E-07 4.30E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 18.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: 343XI307|L2 (343PZ305+0,5)

The information and reliability data underneath describe the 343XI307|L2 (343PZ305+0,5) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 343XI307¦L2 (343PZ305+0,5) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343PZ305, 343PZ307, 343PZ308 |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308

The following table shows the equipment that defines sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 1473 Sensor Leg 1-3: 343PZ305, 343PZ307, 343PZ308 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 343PZ305, 343PZ307, 343PZ308.

Table 1474 Reliability Data Sensor Leg 1-3 343PZ305, 343PZ307, 343PZ308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 5.21E-08 | - - | 8.00E-08 4.47E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 15.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1475 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.79E-06 | 2 | N/A | 37.91 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 1476 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1477 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5)) Safety Instrumented Function is quantified as follows.

Table 1478 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.54E-03 | 2 | N/A | 1389.63 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Close 252SV562

The information and reliability data underneath describe the Close 252SV562 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 252SV562 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1479 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1480 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 13.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-132 SIL3 | High pressure downstream of 356RV558 => close 356SV563 & 356SV564 (1oo2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL3 ¦ High pressure downstream of 356RV558 => close 356SV563 & 356SV564 (1oo2) |
| --- | --- |
| SIF Tag | SIF-132 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 3 with RRF ≥ 1000 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 3 with RRF = 1127.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 10 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Batch Operation: | Yes |
| Batch Duration: | 2 month(s) |
| Time Between Batches: | 2 month(s) |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1481 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.87E-04 | 1127.6 | 3 | 3 | N/A | 48.9 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function is quantified as follows.

Table 1482 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.40E-05 | 3 | N/A | 151.73 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 356PI355 356PI353

The information and reliability data underneath describe the 356PI355 356PI353 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 356PI355 356PI353 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 356PI355, 356PI353 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Sensor Leg 1-2: 356PI355, 356PI353

The following table shows the equipment that defines sensor leg 1-2 356PI355, 356PI353.

Table 1483 Sensor Leg 1-2: 356PI355, 356PI353 Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL3 [AnalogIn] | 2013.1.02 | - | - | B | 3 |
| Analog In Module: AI880A/TU844/845/TY801 | 2013.1.02 | - | - | B | 3 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 356PI355, 356PI353.

Table 1484 Reliability Data Sensor Leg 1-2 356PI355, 356PI353

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - - | - 3.96E-07 | - - | 6.53E-08 1.17E-07 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL3 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 91.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function is quantified as follows.

Table 1485 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.25E-08 | 3 | N/A | 144 | 1 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL3 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL3 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 1 |
| -factor [%]: | 1 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

Table 1486 ABB AC800M High Integrity SIL3 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL3 | 2013.1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL3.

Table 1487 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL3

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/TP830 SM811/TP868 (SM810/P855) | 4.51E-07 | 7.54E-07 | 1.46E-06 | 5.56E-11 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: 1*SD821 + 1*SS823 + 2*MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2) Safety Instrumented Function is quantified as follows.

Table 1488 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.53E-04 | 3 | N/A | 144.66 | 1 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 356SV563 & 356SV564 (1oo2)

The information and reliability data underneath describe the close 356SV563 & 356SV564 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 356SV563 & 356SV564 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 356SV563, 356SV564 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 68.9 |
| Proof Test Execution: | Offline |
| Batches before Proof Test: | 3 |

##### Final Element Leg 1-2: 356SV563, 356SV564

The following table shows the equipment that defines final element leg 1-2 356SV563, 356SV564.

Table 1489 Final Element Leg 1-2: 356SV563, 356SV564 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2013.1.02 | - | - | B | 3 |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 2013.1.02 | - | - | B | 3 |
| Herion 97105 1oo2 |  | ü | - | A | 3 |
| Flowserve Norbro 33-25..33-50; 40R-05..40R-42; 40-45..40-50, SR | 2020.Q4.02 | ü | - | A | 3 |
| Flowserve Worcester Series 44 Ball Valve | 2011.4.03 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 356SV563, 356SV564.

Table 1490 Reliability Data Final Element Leg 1-2 356SV563, 356SV564

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL3 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Herion 97105 1oo2 | - | - | - | 3.01E-09 | - | - | - |
| Flowserve Norbro 33-25..33-50; 40R-05..40R-42; 40-45..40-50, SR | - | 3.05E-07 | - | 3.72E-07 | - | - | 1.56E-06 |
| Flowserve Worcester Series 44 Ball Valve | - | - | - | 4.51E-07 | - | - | 9.12E-07 |
|  |  |  |  |  | SFF [%] |  | 60.7 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the End of Batch Test performed.

# SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 High level (347LZ302) in Absorber (347YM100) |
| --- | --- |
| SIF Tag | SIF-133 |
| SIF Description: | High level (347LZ302 H1) in absorber (347YM100) close 347SV509 (USY feed water) and stop 354PU101 This SIF is only active while CO2 removal unit is running in the process gas loop Lägesbrytare "CO2 kopplad mot processgaskompressor" GS2 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 494 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1491 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 2.02E-03 | 494 | 2 | 2 | N/A | 18.81 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 1492 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.05E-03 | 2 | N/A | 263.52 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High level in Absorber

The information and reliability data underneath describe the High level in Absorber sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High level in Absorber |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LZ302 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 92.2 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LZ302

The following table shows the equipment that defines sensor leg 1-1 347LZ302.

Table 1493 Sensor Leg 1-1: 347LZ302 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LZ302.

Table 1494 Reliability Data Sensor Leg 1-1 347LZ302

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 8.39E-08 9.01E-08 | 8.53E-08 8.53E-08 | 6.21E-09 - | 5.92E-08 5.92E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 81.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 1495 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1496 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1497 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100) Safety Instrumented Function is quantified as follows.

Table 1498 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.68E-04 | 2 | N/A | 1162.95 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: USY feed water

The information and reliability data underneath describe the USY feed water final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | USY feed water |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 347SV509 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 85 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 347SV509

The following table shows the equipment that defines final element leg 1-1 347SV509.

Table 1499 Final Element Leg 1-1: 347SV509 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Metso Norgren |  | - | - | A | 3 |
| Metso VPVL |  | - | - | A | 3 |
| Metso 7000 9000 |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 347SV509.

Table 1500 Reliability Data Final Element Leg 1-1 347SV509

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Metso Norgren | - | 2.28E-09 | - | 2.28E-11 | - | - | - |
| Metso VPVL | - | 4.25E-08 | - | 8.49E-09 | - | - | - |
| Metso 7000 9000 | - | 7.57E-08 | - | 4.84E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 79.8 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Top gas compressor (354PU101)

The information and reliability data underneath describe the Top gas compressor (354PU101) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Top gas compressor (354PU101) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 1501 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 1502 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| --- | --- |
| SIF Tag | SIF-134 |
| SIF Description: | SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 642.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1503 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.56E-03 | 642.4 | 2 | 2 | N/A | 18.42 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 1504 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.40E-03 | 2 | N/A | 554.98 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Gastemp eft. kylare red.gaskompressor

The information and reliability data underneath describe the Gastemp eft. kylare red.gaskompressor sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Gastemp eft. kylare red.gaskompressor |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 354TI410 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 354TI410

The following table shows the equipment that defines sensor leg 1-1 354TI410.

Table 1505 Sensor Leg 1-1: 354TI410 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 354TI410.

Table 1506 Reliability Data Sensor Leg 1-1 354TI410

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 62.6 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 1507 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.31E-06 | 2 | N/A | 19.43 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1508 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1509 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2) Safety Instrumented Function is quantified as follows.

Table 1510 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Top gas compressor (354PU101)

The information and reliability data underneath describe the Top gas compressor (354PU101) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Top gas compressor (354PU101) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 1511 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 1512 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-135 SIL1 High level (347LS305) filter separator 347SE101

This chapter details the SIL Verification results, selections, and assumptions for the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 High level (347LS305) filter separator 347SE101 |
| --- | --- |
| SIF Tag | SIF-135 |
| SIF Description: | High level ( 347LS305 H1) filter separator 347SE101 This SIF is only active while CO2 removal unit is running in the process gas loop Lägesbrytare "CO2 kopplad mot processgaskompressor" GS2 |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 734.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1513 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.36E-03 | 734.1 | 2 | 2 | N/A | 18.8 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function is quantified as follows.

Table 1514 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.20E-03 | 2 | N/A | 272.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High level filter separator 347SE101

The information and reliability data underneath describe the High level filter separator 347SE101 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High level filter separator 347SE101 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 347LS305 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 91.9 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 347LS305

The following table shows the equipment that defines sensor leg 1-1 347LS305.

Table 1515 Sensor Leg 1-1: 347LS305 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 | 2006.2.02 | - | - | B | - |
| PR Electronics 9202, relay output | 2015.2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 347LS305.

Table 1516 Reliability Data Sensor Leg 1-1 347LS305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Liquiphant M/S + FEL 58 | - - | - - | - - | 6.56E-08 7.83E-08 | 8.30E-08 8.30E-08 | 1.27E-08 - | 7.27E-08 7.27E-08 | - - | 2.00E-09 2.00E-09 | 1.02E-07 1.02E-07 |
| PR Electronics 9202, relay output | - - | - - | - - | - 9.10E-08 | 1.40E-07 1.40E-07 | 9.10E-08 - | 4.60E-08 4.60E-08 | 3.90E-08 3.90E-08 | 1.00E-09 1.00E-09 | 1.50E-07 1.50E-07 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 2.38E-08 | 3.45E-09 3.45E-09 | 1.66E-08 - | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 79.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function is quantified as follows.

Table 1517 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1518 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1519 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-135 SIL1 High level (347LS305) filter separator 347SE101 Safety Instrumented Function is quantified as follows.

Table 1520 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.53E-04 | 2 | N/A | 990.72 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Top gas compressor (354PU101)

The information and reliability data underneath describe the Top gas compressor (354PU101) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Top gas compressor (354PU101) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 354PU101 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 354PU101

The following table shows the equipment that defines final element leg 1-1 354PU101.

Table 1521 Final Element Leg 1-1: 354PU101 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 354PU101.

Table 1522 Reliability Data Final Element Leg 1-1 354PU101

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 89.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI340 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-136 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1523 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1524 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1525 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1526 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1527 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1528 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1529 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1530 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1531 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1532 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI341 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-137 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1533 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1534 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1535 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1536 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1537 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1538 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1539 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1540 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1541 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1542 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI342 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-138 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1543 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1544 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1545 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1546 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1547 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1548 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1549 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1550 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1551 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1552 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI343 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-139 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1553 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1554 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1555 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1556 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1557 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1558 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1559 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1560 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1561 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1562 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI344 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-140 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1563 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1564 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1565 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1566 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1567 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1568 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1569 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1570 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1571 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1572 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002

This chapter details the SIL Verification results, selections, and assumptions for the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ High temperature Kanthal 344TI345 => stop heater 344HE002 |
| --- | --- |
| SIF Tag | SIF-141 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 153.5 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 17 Nov 2020 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1573 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 6.51E-03 | 153.5 | 2 | 2 | N/A | 18.34 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1574 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.72E-04 | 2 | N/A | 152.59 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High temperature Kanthal 344TI340 -> 345

The information and reliability data underneath describe the High temperature Kanthal 344TI340 -> 345 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High temperature Kanthal 344TI340 -> 345 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 344TI34* |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 344TI34*

The following table shows the equipment that defines sensor leg 1-1 344TI34*.

Table 1575 Sensor Leg 1-1: 344TI34* Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 2019.4.01 | - | - | B | 3 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 344TI34*.

Table 1576 Reliability Data Sensor Leg 1-1 344TI34*

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR electronics PR5435 / PR5437, Single, 4..20mA | 4.90E-08 - | 1.70E-08 - | 3.58E-07 - | - - | - 3.75E-07 | - - | 2.70E-08 7.60E-08 | 1.90E-08 1.90E-08 | 1.10E-08 1.10E-08 | 2.13E-07 2.13E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1577 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1578 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1579 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002 Safety Instrumented Function is quantified as follows.

Table 1580 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 344HE002

The information and reliability data underneath describe the Stop 344HE002 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 344HE002 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 344HE002 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 344HE002

The following table shows the equipment that defines final element leg 1-1 344HE002.

Table 1581 Final Element Leg 1-1: 344HE002 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 344HE002.

Table 1582 Reliability Data Final Element Leg 1-1 344HE002

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater

This chapter details the SIL Verification results, selections, and assumptions for the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater |
| --- | --- |
| SIF Tag | SIF-143 |
| SIF Description: | SIL1¦343HV500_Ej GSO och/eller 343HV501_Ej GSS - SIL1 Flöde reduktionsgas till PGH (Exklusivt) => Close Avstängningsventil 1 H2 till brännare PGH (341SV665 SIL2) Close Avstängningsventil 2 H2 till brännare PGH (341SV667 SIL2) Close Avstängningsventil 1 NG till brännare PGH (252SV544 SIL2) Close Avstängningsventil 2 NG till brännare PGH (252SV546 SIL2) Close Avstängningsventil 1 O2 inj. (251SV555 SIL2) Close Avstängningsventil 2 O2 inj. (251SV556 SIL2) Endast 1 bränsle åt gången. |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 140.7 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 04 Oct 2019 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On same I/O module |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1583 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.11E-03 | 140.7 | 2 | 2 | N/A | 19.81 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function is quantified as follows.

Table 1584 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.34E-06 | 3 | N/A | 2409.2 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: SIL1 | 343HV500_Ej GSO och/eller 343HV501_Ej GSS

The information and reliability data underneath describe the SIL1 | 343HV500_Ej GSO och/eller 343HV501_Ej GSS sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIL1 ¦ 343HV500_Ej GSO och/eller 343HV501_Ej GSS |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 343HV500_GSO, 343HV501_GSS |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-2: 343HV500_GSO, 343HV501_GSS

The following table shows the equipment that defines sensor leg 1-2 343HV500_GSO, 343HV501_GSS.

Table 1585 Sensor Leg 1-2: 343HV500_GSO, 343HV501_GSS Details

| Sensor Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Pepperl+Fuchs NCN3-F25*-SN4*** | 2006.Q2.02 | - | - | A | - |
| ABB AC800M High Integrity SIL2 [DigitalIn] | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-2 343HV500_GSO, 343HV501_GSS.

Table 1586 Reliability Data Sensor Leg 1-2 343HV500_GSO, 343HV501_GSS

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Pepperl+Fuchs NCN3-F25*-SN4*** | - - | - - | - - | - - | 1.43E-08 1.43E-08 | - - | 1.07E-08 1.07E-08 | - - | - - | 4.74E-09 4.74E-09 |
| ABB AC800M High Integrity SIL2 [DigitalIn] | - - | - - | - - | 7.19E-09 7.19E-09 | 3.45E-09 3.45E-09 | 1.66E-08 1.66E-08 | 1.66E-12 1.66E-12 | - - | - - | 9.23E-09 9.23E-09 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 79.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function is quantified as follows.

Table 1587 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.90E-06 | 2 | N/A | 20.62 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1588 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1589 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital In Module: DI880/TU842/843 | 1.94E-07 | 4.80E-09 | 2.16E-07 | 1.15E-10 | 3.89E-08 | 3.93E-10 | 1.86E-07 |
| Channel: Digitial In | 7.19E-09 | 3.45E-09 | 1.66E-08 | 1.66E-12 |  |  | 9.23E-09 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater Safety Instrumented Function is quantified as follows.

Table 1590 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.09E-03 | 3 | N/A | 642.01 | 1 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: | 10 |

#### Final Element Group 1: H2 till brännare PGH

The information and reliability data underneath describe the H2 till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2 till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV665, 341SV667 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 341SV665, 341SV667

The following table shows the equipment that defines final element leg 1-2 341SV665, 341SV667.

Table 1591 Final Element Leg 1-2: 341SV665, 341SV667 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 341SV665, 341SV667.

Table 1592 Reliability Data Final Element Leg 1-2 341SV665, 341SV667

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: NG till brännare PGH

The information and reliability data underneath describe the NG till brännare PGH final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | NG till brännare PGH |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 252SV544, 252SV546 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 252SV544, 252SV546

The following table shows the equipment that defines final element leg 1-2 252SV544, 252SV546.

Table 1593 Final Element Leg 1-2: 252SV544, 252SV546 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 252SV544, 252SV546.

Table 1594 Reliability Data Final Element Leg 1-2 252SV544, 252SV546

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: O2 inj

The information and reliability data underneath describe the O2 inj final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | O2 inj |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 251SV555, 251SV556 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 251SV555, 251SV556

The following table shows the equipment that defines final element leg 1-2 251SV555, 251SV556.

Table 1595 Final Element Leg 1-2: 251SV555, 251SV556 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | Yes |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 251SV555, 251SV556.

Table 1596 Reliability Data Final Element Leg 1-2 251SV555, 251SV556

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 1.90E-06 | - | - | 6.72E-07 |
|  |  |  |  |  | SFF [%] |  | 5.9 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200

This chapter details the SIL Verification results, selections, and assumptions for the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦ High tempertature in (356TI308) => trip 356HE200 |
| --- | --- |
| SIF Tag | SIF-144 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 210.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1597 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 4.76E-03 | 210.1 | 2 | 2 | N/A | 17.68 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function is quantified as follows.

Table 1598 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.15E-04 | 2 | N/A | 116.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High tempertature in (356TI308)

The information and reliability data underneath describe the High tempertature in (356TI308) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High tempertature in (356TI308) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 356TI308 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 356TI308

The following table shows the equipment that defines sensor leg 1-1 356TI308.

Table 1599 Sensor Leg 1-1: 356TI308 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 356TI308.

Table 1600 Reliability Data Sensor Leg 1-1 356TI308

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - 2.05E-07 | - - | - - | 7.40E-08 7.40E-08 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function is quantified as follows.

Table 1601 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1602 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1603 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200 Safety Instrumented Function is quantified as follows.

Table 1604 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.14E-03 | 2 | N/A | 90.82 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 356HE200

The information and reliability data underneath describe the Stop 356HE200 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 356HE200 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1605 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1606 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-301 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 724.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1607 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.38E-03 | 724.9 | 2 | 2 | N/A | 19.96 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1608 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperature stage 1 (423TI301)

The information and reliability data underneath describe the Temperature stage 1 (423TI301) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperature stage 1 (423TI301) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423TI301 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423TI301

The following table shows the equipment that defines sensor leg 1-1 423TI301.

Table 1609 Sensor Leg 1-1: 423TI301 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423TI301.

Table 1610 Reliability Data Sensor Leg 1-1 423TI301

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1611 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1612 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1613 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1614 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1615 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1616 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-302 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 724.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1617 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.38E-03 | 724.9 | 2 | 2 | N/A | 19.96 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1618 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperature stage 2 (423TI302)

The information and reliability data underneath describe the Temperature stage 2 (423TI302) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperature stage 2 (423TI302) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423TI302 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423TI302

The following table shows the equipment that defines sensor leg 1-1 423TI302.

Table 1619 Sensor Leg 1-1: 423TI302 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423TI302.

Table 1620 Reliability Data Sensor Leg 1-1 423TI302

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1621 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1622 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1623 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1624 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1625 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1626 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-303 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 724.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1627 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.38E-03 | 724.9 | 2 | 2 | N/A | 19.96 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1628 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.21E-03 | 2 | N/A | 117.1 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Temperature stage 3 (423TI303)

The information and reliability data underneath describe the Temperature stage 3 (423TI303) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Temperature stage 3 (423TI303) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423TI303 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423TI303

The following table shows the equipment that defines sensor leg 1-1 423TI303.

Table 1629 Sensor Leg 1-1: 423TI303 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423TI303.

Table 1630 Reliability Data Sensor Leg 1-1 423TI303

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - 2.00E-07 | - - | - - | 1.07E-07 1.07E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.5 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1631 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1632 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1633 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1634 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1635 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1636 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-304 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1806.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1637 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 5.54E-04 | 1806.2 | 3 | 2 | N/A | 19.13 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1638 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.85E-04 | 2 | N/A | 93.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: High Pressure compressor (423PI304)

The information and reliability data underneath describe the High Pressure compressor (423PI304) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | High Pressure compressor (423PI304) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PI304 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PI304

The following table shows the equipment that defines sensor leg 1-1 423PI304.

Table 1639 Sensor Leg 1-1: 423PI304 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PI304.

Table 1640 Reliability Data Sensor Leg 1-1 423PI304

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 | 5.21E-08 - | 6.85E-08 - | 3.27E-07 - | - 4.48E-07 | - - | - - | 6.53E-08 6.53E-08 | - - | 1.00E-08 1.00E-08 | 3.03E-07 3.03E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.1 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1641 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1642 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1643 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1644 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1645 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1646 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-305 SIL1|341TI390 HH => Stop 341HE269

This chapter details the SIL Verification results, selections, and assumptions for the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦341TI390 HH => Stop 341HE269 |
| --- | --- |
| SIF Tag | SIF-305 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 122.6 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1647 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.15E-03 | 122.6 | 2 | 2 | N/A | 18.91 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function is quantified as follows.

Table 1648 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.52E-03 | 2 | N/A | 203 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 341TI390 HH

The information and reliability data underneath describe the 341TI390 HH sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 341TI390 HH |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341TI390 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341TI390

The following table shows the equipment that defines sensor leg 1-1 341TI390.

Table 1649 Sensor Leg 1-1: 341TI390 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| PR Electronics 9106, 1 active in/1 active out | 2014.4.03 | - | - | A | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341TI390.

Table 1650 Reliability Data Sensor Leg 1-1 341TI390

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - - | - 1.63E-07 | - - | 7.40E-08 1.16E-07 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| PR Electronics 9106, 1 active in/1 active out | 1.46E-07 - | 2.70E-08 - | - - | - - | - 2.70E-08 | - - | 4.10E-08 1.87E-07 | - - | - - | 1.77E-07 1.77E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 76.9 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function is quantified as follows.

Table 1651 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1652 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1653 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-305 SIL1|341TI390 HH => Stop 341HE269 Safety Instrumented Function is quantified as follows.

Table 1654 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 5.64E-03 | 2 | N/A | 90.96 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: Stop 341HE269

The information and reliability data underneath describe the Stop 341HE269 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Stop 341HE269 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | Final Element Leg |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: Final Element Leg

The following table shows the equipment that defines final element leg 1-1 Final Element Leg.

Table 1655 Final Element Leg 1-1: Final Element Leg Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| PSR-PS20 |  | - | - | A | 3 |
| Generic Motor Contactor | 2020.Q4.01 | - | - | A | - |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 Final Element Leg.

Table 1656 Reliability Data Final Element Leg 1-1 Final Element Leg

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| PSR-PS20 | - | - | - | - | - | - | - |
| Generic Motor Contactor | - | 7.50E-07 | - | 5.00E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 77.5 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-306 SIL1| Leakage detection 341XI687

This chapter details the SIL Verification results, selections, and assumptions for the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦ Leakage detection 341XI687 |
| --- | --- |
| SIF Tag | SIF-306 |
| SIF Description: | Close 421SV501, block and bleed 411SV501 and SV502, as well as 341SV686 should close. and open SSAB bleed." |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 30.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1657 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.30E-02 | 30.3 | 1 | 2 | N/A | 26.21 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function is quantified as follows.

Table 1658 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.22E-03 | 2 | N/A | 1179.31 | 0 | 2 |

| Number of Sensor group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Sensor Group 1: Leakage detection 341XI687 Preassure

The information and reliability data underneath describe the Leakage detection 341XI687 Preassure sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Leakage detection 341XI687 Preassure |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PI687, 411PI301, 421PI305 |
| Voting within group: | 3oo3 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 341PI687, 411PI301, 421PI305

The following table shows the equipment that defines sensor leg 1-3 341PI687, 411PI301, 421PI305.

Table 1659 Sensor Leg 1-3: 341PI687, 411PI301, 421PI305 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 341PI687, 411PI301, 421PI305.

Table 1660 Reliability Data Sensor Leg 1-3 341PI687, 411PI301, 421PI305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - 4.19E-07 | - - | - - | 8.00E-08 8.00E-08 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

#### Sensor Group 2: Leakage detection 341XI687 Flow

The information and reliability data underneath describe the Leakage detection 341XI687 Flow sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Leakage detection 341XI687 Flow |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341FI687, 411FI502, 421FI301 |
| Voting within group: | 3oo3 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 341FI687, 411FI502, 421FI301

The following table shows the equipment that defines sensor leg 1-3 341FI687, 411FI502, 421FI301.

Table 1661 Sensor Leg 1-3: 341FI687, 411FI502, 421FI301 Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser PROMASS 83 standard | 2011.Q4.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 341FI687, 411FI502, 421FI301.

Table 1662 Reliability Data Sensor Leg 1-3 341FI687, 411FI502, 421FI301

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser PROMASS 83 standard | 9.70E-08 - | 2.10E-08 - | 1.06E-06 - | - 1.18E-06 | - - | - - | 1.77E-07 1.77E-07 | 4.10E-08 4.10E-08 | 1.00E-09 1.00E-09 | 3.23E-07 3.23E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 92.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function is quantified as follows.

Table 1663 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1664 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1665 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-306 SIL1| Leakage detection 341XI687 Safety Instrumented Function is quantified as follows.

Table 1666 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.89E-02 | 2 | N/A | 3025.17 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: 411SV501 & 411SV502

The information and reliability data underneath describe the 411SV501 & 411SV502 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 411SV501 & 411SV502 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 411SV501, 411SV502 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 411SV501, 411SV502

The following table shows the equipment that defines final element leg 1-2 411SV501, 411SV502.

Table 1667 Final Element Leg 1-2: 411SV501, 411SV502 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 411SV501, 411SV502.

Table 1668 Reliability Data Final Element Leg 1-2 411SV501, 411SV502

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: 421SV501 & 341SV686

The information and reliability data underneath describe the 421SV501 & 341SV686 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 421SV501 & 341SV686 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV501, 341SV686 |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 421SV501

The following table shows the equipment that defines final element leg 1 421SV501.

Table 1669 Final Element Leg 1: 421SV501 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 421SV501.

Table 1670 Reliability Data Final Element Leg 1 421SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 341SV686

The following table shows the equipment that defines final element leg 2 341SV686.

Table 1671 Final Element Leg 2: 341SV686 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 341SV686.

Table 1672 Reliability Data Final Element Leg 2 341SV686

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-308 SIL1|421PI305 LL => close 421SV501

This chapter details the SIL Verification results, selections, and assumptions for the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦421PI305 LL => close 421SV501 |
| --- | --- |
| SIF Tag | SIF-308 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 118.1 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1673 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.47E-03 | 118.1 | 2 | 2 | N/A | 19.09 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function is quantified as follows.

Table 1674 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.71E-04 | 2 | N/A | 95.6 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 421PI305 LL

The information and reliability data underneath describe the 421PI305 LL sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 421PI305 LL |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 421PI305 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 421PI305

The following table shows the equipment that defines sensor leg 1-1 421PI305.

Table 1675 Sensor Leg 1-1: 421PI305 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 421PI305.

Table 1676 Reliability Data Sensor Leg 1-1 421PI305

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - 4.19E-07 | - - | - - | 8.00E-08 8.00E-08 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function is quantified as follows.

Table 1677 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1678 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1679 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-308 SIL1|421PI305 LL => close 421SV501 Safety Instrumented Function is quantified as follows.

Table 1680 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.00E-03 | 2 | N/A | 202.18 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 421SV501

The information and reliability data underneath describe the close 421SV501 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 421SV501 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV501 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV501

The following table shows the equipment that defines final element leg 1-1 421SV501.

Table 1681 Final Element Leg 1-1: 421SV501 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV501.

Table 1682 Reliability Data Final Element Leg 1-1 421SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2¦ 423PI301 LL => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-309 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 3287.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1683 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.04E-04 | 3287.3 | 3 | 2 | N/A | 23.49 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1684 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.36E-04 | 3 | N/A | 988.53 | 1 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 423PI301 LL

The information and reliability data underneath describe the 423PI301 LL sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 423PI301 LL |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PI301A, 423PI301B, 423PI301C |
| Voting within group: | 2oo3 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-3: 423PI301A, 423PI301B, 423PI301C

The following table shows the equipment that defines sensor leg 1-3 423PI301A, 423PI301B, 423PI301C.

Table 1685 Sensor Leg 1-3: 423PI301A, 423PI301B, 423PI301C Details

| Sensor Leg 1-3 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-3 423PI301A, 423PI301B, 423PI301C.

Table 1686 Reliability Data Sensor Leg 1-3 423PI301A, 423PI301B, 423PI301C

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 3.50E-07 | - - | 8.00E-08 1.49E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 88.8 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1687 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1688 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1689 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1690 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1691 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1692 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-310 SIL2|421TI304 HH => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2¦421TI304 HH => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-310 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 633.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1693 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.58E-03 | 633.8 | 2 | 2 | N/A | 21.54 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1694 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.41E-03 | 2 | N/A | 205.17 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 421TI304 HH

The information and reliability data underneath describe the 421TI304 HH sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 421TI304 HH |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 421TI304 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 421TI304

The following table shows the equipment that defines sensor leg 1-1 421TI304.

Table 1695 Sensor Leg 1-1: 421TI304 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser iTemp TMT 182 | 2006.2.02 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 421TI304.

Table 1696 Reliability Data Sensor Leg 1-1 421TI304

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser iTemp TMT 182 | 1.66E-08 - | 9.16E-08 - | 9.18E-08 - | - - | - 1.83E-07 | - - | 1.07E-07 1.24E-07 | - - | 1.22E-09 1.22E-09 | 9.78E-08 9.78E-08 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 89.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1697 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1698 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1699 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1700 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1701 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1702 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-311 SIL1| 421PI301 > H2 => close 421SV503

This chapter details the SIL Verification results, selections, and assumptions for the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1¦ 421PI301 > H2 => close 421SV503 |
| --- | --- |
| SIF Tag | SIF-311 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 113.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1703 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 8.78E-03 | 113.8 | 2 | 2 | N/A | 20.66 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function is quantified as follows.

Table 1704 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 7.89E-04 | 2 | N/A | 154.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: 421PI301

The information and reliability data underneath describe the 421PI301 sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 421PI301 |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 421PI301 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 421PI301

The following table shows the equipment that defines sensor leg 1-1 421PI301.

Table 1705 Sensor Leg 1-1: 421PI301 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 421PI301.

Table 1706 Reliability Data Sensor Leg 1-1 421PI301

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - - | - 3.67E-07 | - - | 8.00E-08 1.32E-07 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 4.28E-09 | 4.28E-13 4.28E-13 | 1.83E-08 1.83E-08 | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 3.69E-07 | 5.00E-10 5.00E-10 | 3.84E-07 3.84E-07 | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 90.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function is quantified as follows.

Table 1707 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1708 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1709 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-311 SIL1|  421PI301 > H2 => close 421SV503 Safety Instrumented Function is quantified as follows.

Table 1710 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 8.00E-03 | 2 | N/A | 202.18 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 421SV503

The information and reliability data underneath describe the close 421SV503 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 421SV503 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV503 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV503

The following table shows the equipment that defines final element leg 1-1 421SV503.

Table 1711 Final Element Leg 1-1: 421SV503 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV503.

Table 1712 Reliability Data Final Element Leg 1-1 421SV503

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB

This chapter details the SIL Verification results, selections, and assumptions for the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB |
| --- | --- |
| SIF Tag | SIF-312 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 64.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1713 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.56E-02 | 64.2 | 1 | 2 | N/A | 20.86 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1714 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.71E-04 | 2 | N/A | 95.6 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck i koksgasledning SSAB LL (411PI302)

The information and reliability data underneath describe the Tryck i koksgasledning SSAB LL (411PI302) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck i koksgasledning SSAB LL (411PI302) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 411PI302 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 411PI302

The following table shows the equipment that defines sensor leg 1-1 411PI302.

Table 1715 Sensor Leg 1-1: 411PI302 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 411PI302.

Table 1716 Reliability Data Sensor Leg 1-1 411PI302

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - 4.19E-07 | - - | - - | 8.00E-08 8.00E-08 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1717 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1718 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1719 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1720 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.51E-02 | 2 | N/A | 2017.84 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: 411SV501 & 411SV502

The information and reliability data underneath describe the 411SV501 & 411SV502 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 411SV501 & 411SV502 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 411SV501, 411SV502 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 411SV501, 411SV502

The following table shows the equipment that defines final element leg 1-2 411SV501, 411SV502.

Table 1721 Final Element Leg 1-2: 411SV501, 411SV502 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 411SV501, 411SV502.

Table 1722 Reliability Data Final Element Leg 1-2 411SV501, 411SV502

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB

This chapter details the SIL Verification results, selections, and assumptions for the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB |
| --- | --- |
| SIF Tag | SIF-313 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 64.2 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1723 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.56E-02 | 64.2 | 1 | 2 | N/A | 20.86 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1724 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.71E-04 | 2 | N/A | 95.6 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck i koksgasledning SSAB HH (411PI302)

The information and reliability data underneath describe the Tryck i koksgasledning SSAB HH (411PI302) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck i koksgasledning SSAB HH (411PI302) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 411PI302 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 411PI302

The following table shows the equipment that defines sensor leg 1-1 411PI302.

Table 1725 Sensor Leg 1-1: 411PI302 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 411PI302.

Table 1726 Reliability Data Sensor Leg 1-1 411PI302

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - 4.19E-07 | - - | - - | 8.00E-08 8.00E-08 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1727 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1728 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1729 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB Safety Instrumented Function is quantified as follows.

Table 1730 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.51E-02 | 2 | N/A | 2017.84 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: 411SV501 & 411SV502

The information and reliability data underneath describe the 411SV501 & 411SV502 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 411SV501 & 411SV502 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 411SV501, 411SV502 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 411SV501, 411SV502

The following table shows the equipment that defines final element leg 1-2 411SV501, 411SV502.

Table 1731 Final Element Leg 1-2: 411SV501, 411SV502 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 411SV501, 411SV502.

Table 1732 Reliability Data Final Element Leg 1-2 411SV501, 411SV502

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686

This chapter details the SIL Verification results, selections, and assumptions for the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 |
| --- | --- |
| SIF Tag | SIF-314 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL TBD with RRF ≥ 1 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 136.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1733 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.30E-03 | 136.9 | 2 | 2 | N/A | 19.09 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function is quantified as follows.

Table 1734 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 4.71E-04 | 2 | N/A | 95.6 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Tryck H2 i pipeline P1 <-> P3 (341PI687)

The information and reliability data underneath describe the Tryck H2 i pipeline P1 <-> P3 (341PI687) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Tryck H2 i pipeline P1 <-> P3 (341PI687) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 341PI687 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 99 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 341PI687

The following table shows the equipment that defines sensor leg 1-1 341PI687.

Table 1735 Sensor Leg 1-1: 341PI687 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 2006.2.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | Low |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 341PI687.

Table 1736 Reliability Data Sensor Leg 1-1 341PI687

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Endress+Hauser Cerabar S PMC71 Standard Exi | 5.21E-08 - | 6.85E-08 - | 2.98E-07 - | - 4.19E-07 | - - | - - | 8.00E-08 8.00E-08 | - - | 1.00E-08 1.00E-08 | 3.82E-07 3.82E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 94.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function is quantified as follows.

Table 1737 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1738 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1739 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 Safety Instrumented Function is quantified as follows.

Table 1740 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.83E-03 | 2 | N/A | 201.94 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 341SV686

The information and reliability data underneath describe the close 341SV686 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 341SV686 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 341SV686 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 341SV686

The following table shows the equipment that defines final element leg 1-1 341SV686.

Table 1741 Final Element Leg 1-1: 341SV686 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 341SV686.

Table 1742 Reliability Data Final Element Leg 1-1 341SV686

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-315 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1276.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1743 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.83E-04 | 1276.4 | 3 | 2 | N/A | 19.94 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1744 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.15E-04 | 2 | N/A | 116.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Motortemperatur lindning 1 (423PU001-TI1)

The information and reliability data underneath describe the Motortemperatur lindning 1 (423PU001-TI1) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Motortemperatur lindning 1 (423PU001-TI1) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PU001-TI1 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PU001-TI1

The following table shows the equipment that defines sensor leg 1-1 423PU001-TI1.

Table 1745 Sensor Leg 1-1: 423PU001-TI1 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PU001-TI1.

Table 1746 Reliability Data Sensor Leg 1-1 423PU001-TI1

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - 2.05E-07 | - - | - - | 7.40E-08 7.40E-08 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1747 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1748 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1749 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1750 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1751 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1752 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-316 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1276.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1753 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.83E-04 | 1276.4 | 3 | 2 | N/A | 19.94 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1754 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.15E-04 | 2 | N/A | 116.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Motortemperatur lindning 2 (423PU001-TI2)

The information and reliability data underneath describe the Motortemperatur lindning 2 (423PU001-TI2) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Motortemperatur lindning 2 (423PU001-TI2) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PU001-TI2 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PU001-TI2

The following table shows the equipment that defines sensor leg 1-1 423PU001-TI2.

Table 1755 Sensor Leg 1-1: 423PU001-TI2 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PU001-TI2.

Table 1756 Reliability Data Sensor Leg 1-1 423PU001-TI2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - 2.05E-07 | - - | - - | 7.40E-08 7.40E-08 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1757 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1758 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1759 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1760 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1761 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1762 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Motortemperatur lindning 3 (423PU001-TI3) => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-317 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1276.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1763 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.83E-04 | 1276.4 | 3 | 2 | N/A | 19.94 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1764 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.15E-04 | 2 | N/A | 116.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Motortemperatur lindning 3 (423PU001-TI3)

The information and reliability data underneath describe the Motortemperatur lindning 3 (423PU001-TI3) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Motortemperatur lindning 3 (423PU001-TI3) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PU001-TI3 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PU001-TI3

The following table shows the equipment that defines sensor leg 1-1 423PU001-TI3.

Table 1765 Sensor Leg 1-1: 423PU001-TI3 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PU001-TI3.

Table 1766 Reliability Data Sensor Leg 1-1 423PU001-TI3

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - 2.05E-07 | - - | - - | 7.40E-08 7.40E-08 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1767 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1768 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1769 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1770 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1771 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1772 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-318 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 883.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1773 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.13E-03 | 883.8 | 2 | 2 | N/A | 20.09 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1774 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 9.63E-04 | 2 | N/A | 121.68 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lagertemperatur (423PU001-TI11)

The information and reliability data underneath describe the Lagertemperatur (423PU001-TI11) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lagertemperatur (423PU001-TI11) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PU001-TI11 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PU001-TI11

The following table shows the equipment that defines sensor leg 1-1 423PU001-TI11.

Table 1775 Sensor Leg 1-1: 423PU001-TI11 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PU001-TI11.

Table 1776 Reliability Data Sensor Leg 1-1 423PU001-TI11

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - - | - 1.63E-07 | - - | 7.40E-08 1.16E-07 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 89.4 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1777 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1778 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1779 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1780 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1781 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1782 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) |
| --- | --- |
| SIF Tag | SIF-319 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 1276.4 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1783 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 7.83E-04 | 1276.4 | 3 | 2 | N/A | 19.94 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1784 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.15E-04 | 2 | N/A | 116.43 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: Lagertemperatur (423PU001-TI12)

The information and reliability data underneath describe the Lagertemperatur (423PU001-TI12) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Lagertemperatur (423PU001-TI12) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | 423PU001-TI12 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 95 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: 423PU001-TI12

The following table shows the equipment that defines sensor leg 1-1 423PU001-TI12.

Table 1785 Sensor Leg 1-1: 423PU001-TI12 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 2014.Q2.04 | - | - | B | - |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 423PU001-TI12.

Table 1786 Reliability Data Sensor Leg 1-1 423PU001-TI12

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| PR Electronics PR5337 / PR 6337, 4-20mA output | 4.20E-08 - | 1.70E-08 - | 1.46E-07 - | - 2.05E-07 | - - | - - | 7.40E-08 7.40E-08 | - - | 1.00E-09 1.00E-09 | 1.17E-07 1.17E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 93.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1787 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1788 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1789 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) Safety Instrumented Function is quantified as follows.

Table 1790 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-04 | 2 | N/A | 218.3 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1791 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1792 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-320 SIL1 | H2-läckage i kulvert (LKAB) HH (KD184-900)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2-läckage i kulvert (LKAB) HH (KD184-900) |
| --- | --- |
| SIF Tag | SIF-320 |
| SIF Description: | 341SV686 H2 avstängning P1 <-> P3 421SV501 LP distributionisolering 411SV501 Avstängning H2 till koksgas SSAB 411SV502 Avstängning H2 till koksgas SSAB |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 32 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1793 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.12E-02 | 32 | 1 | 2 | N/A | 13.73 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function is quantified as follows.

Table 1794 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.36E-03 | 2 | N/A | 28.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: H2-läckage i kulvert (LKAB) HH (KD184-900)

The information and reliability data underneath describe the H2-läckage i kulvert (LKAB) HH (KD184-900) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2-läckage i kulvert (LKAB) HH (KD184-900) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | KD184-900 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: KD184-900

The following table shows the equipment that defines sensor leg 1-1 KD184-900.

Table 1795 Sensor Leg 1-1: KD184-900 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Dräger Polytron 8200, 4-20mA sink | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 KD184-900.

Table 1796 Reliability Data Sensor Leg 1-1 KD184-900

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Dräger Polytron 8200, 4-20mA sink | 1.70E-08 - | 1.40E-08 - | 3.26E-06 - | - 3.29E-06 | - - | - - | 2.09E-07 2.09E-07 | - - | 1.40E-08 1.40E-08 | 1.45E-07 1.45E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function is quantified as follows.

Table 1797 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1798 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1799 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900) Safety Instrumented Function is quantified as follows.

Table 1800 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.89E-02 | 2 | N/A | 3025.17 | 0 | 2 |

| Number of Final Element group(s): | 2 |
| --- | --- |
| Voting between groups: | 2oo2 |
| -factor [%]: |  |

#### Final Element Group 1: 411SV501 & 411SV502

The information and reliability data underneath describe the 411SV501 & 411SV502 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 411SV501 & 411SV502 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 411SV501, 411SV502 |
| Voting within group: | 2oo2 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 411SV501, 411SV502

The following table shows the equipment that defines final element leg 1-2 411SV501, 411SV502.

Table 1801 Final Element Leg 1-2: 411SV501, 411SV502 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 411SV501, 411SV502.

Table 1802 Reliability Data Final Element Leg 1-2 411SV501, 411SV502

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: 421SV501 & 341SV686

The information and reliability data underneath describe the 421SV501 & 341SV686 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | 421SV501 & 341SV686 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV501, 341SV686 |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 421SV501

The following table shows the equipment that defines final element leg 1 421SV501.

Table 1803 Final Element Leg 1: 421SV501 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 421SV501.

Table 1804 Reliability Data Final Element Leg 1 421SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 341SV686

The following table shows the equipment that defines final element leg 2 341SV686.

Table 1805 Final Element Leg 2: 341SV686 Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Transworld Mars |  | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 341SV686.

Table 1806 Reliability Data Final Element Leg 2 341SV686

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Transworld Mars | - | - | - | 3.73E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 49.2 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2-läckage i kompressorstation HH (KD184-901) |
| --- | --- |
| SIF Tag | SIF-321 |
| SIF Description: | Close 421SV501 Close 421SV503 Trip 423PU001-STO |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 54.3 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1807 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.84E-02 | 54.3 | 1 | 2 | N/A | 13.31 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function is quantified as follows.

Table 1808 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.36E-03 | 2 | N/A | 28.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: H2-läckage i kompressorstation HH (KD184-901)

The information and reliability data underneath describe the H2-läckage i kompressorstation HH (KD184-901) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2-läckage i kompressorstation HH (KD184-901) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | KD184-901 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: KD184-901

The following table shows the equipment that defines sensor leg 1-1 KD184-901.

Table 1809 Sensor Leg 1-1: KD184-901 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Dräger Polytron 8200, 4-20mA sink | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 KD184-901.

Table 1810 Reliability Data Sensor Leg 1-1 KD184-901

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Dräger Polytron 8200, 4-20mA sink | 1.70E-08 - | 1.40E-08 - | 3.26E-06 - | - 3.29E-06 | - - | - - | 2.09E-07 2.09E-07 | - - | 1.40E-08 1.40E-08 | 1.45E-07 1.45E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function is quantified as follows.

Table 1811 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1812 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1813 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901) Safety Instrumented Function is quantified as follows.

Table 1814 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.61E-02 | 2 | N/A | 380.73 | 0 | 2 |

| Number of Final Element group(s): | 3 |
| --- | --- |
| Voting between groups: | 3oo3 |
| -factor [%]: |  |

#### Final Element Group 1: vätgaslager kompressor (423PU001)

The information and reliability data underneath describe the vätgaslager kompressor (423PU001) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | vätgaslager kompressor (423PU001) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423PU001 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 423PU001

The following table shows the equipment that defines final element leg 1-1 423PU001.

Table 1815 Final Element Leg 1-1: 423PU001 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 423PU001.

Table 1816 Reliability Data Final Element Leg 1-1 423PU001

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: close 421SV503

The information and reliability data underneath describe the close 421SV503 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 421SV503 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV503 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV503

The following table shows the equipment that defines final element leg 1-1 421SV503.

Table 1817 Final Element Leg 1-1: 421SV503 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV503.

Table 1818 Reliability Data Final Element Leg 1-1 421SV503

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: close 421SV501

The information and reliability data underneath describe the close 421SV501 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 421SV501 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV501 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV501

The following table shows the equipment that defines final element leg 1-1 421SV501.

Table 1819 Final Element Leg 1-1: 421SV501 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV501.

Table 1820 Reliability Data Final Element Leg 1-1 421SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) |
| --- | --- |
| SIF Tag | SIF-322 |
| SIF Description: | Close 421SV501 & Trip 423PU001-STO (2oo2) Close 421SV505 & Close 421SV517 (1oo2) Close 421SV506 & Close 421SV518 (1oo2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 52.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1821 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.89E-02 | 52.9 | 1 | 2 | N/A | 13.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function is quantified as follows.

Table 1822 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.36E-03 | 2 | N/A | 28.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: H2-läckage i tunnelmynning (tunnelport) HH (KD184-910)

The information and reliability data underneath describe the H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | KD184-910 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: KD184-910

The following table shows the equipment that defines sensor leg 1-1 KD184-910.

Table 1823 Sensor Leg 1-1: KD184-910 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Dräger Polytron 8200, 4-20mA sink | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 KD184-910.

Table 1824 Reliability Data Sensor Leg 1-1 KD184-910

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Dräger Polytron 8200, 4-20mA sink | 1.70E-08 - | 1.40E-08 - | 3.26E-06 - | - 3.29E-06 | - - | - - | 2.09E-07 2.09E-07 | - - | 1.40E-08 1.40E-08 | 1.45E-07 1.45E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function is quantified as follows.

Table 1825 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1826 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1827 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) Safety Instrumented Function is quantified as follows.

Table 1828 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-02 | 2 | N/A | 2206.69 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Close 423SV501 &  Trip 423PU001-STO (2oo2)

The information and reliability data underneath describe the Close 423SV501 &  Trip 423PU001-STO (2oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 423SV501 & Trip 423PU001-STO (2oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423SV501, 423PU001-STO |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 423SV501

The following table shows the equipment that defines final element leg 1 423SV501.

Table 1829 Final Element Leg 1: 423SV501 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 423SV501.

Table 1830 Reliability Data Final Element Leg 1 423SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 423PU001-STO

The following table shows the equipment that defines final element leg 2 423PU001-STO.

Table 1831 Final Element Leg 2: 423PU001-STO Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 423PU001-STO.

Table 1832 Reliability Data Final Element Leg 2 423PU001-STO

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close 421SV505 & Close 421SV517 (1oo2)

The information and reliability data underneath describe the Close 421SV505 & Close 421SV517 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV505 & Close 421SV517 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV505, 421SV517 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV505, 421SV517

The following table shows the equipment that defines final element leg 1-2 421SV505, 421SV517.

Table 1833 Final Element Leg 1-2: 421SV505, 421SV517 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV505, 421SV517.

Table 1834 Reliability Data Final Element Leg 1-2 421SV505, 421SV517

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Close 421SV506  & Close 421SV518 (1oo2)

The information and reliability data underneath describe the Close 421SV506  & Close 421SV518 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV506 & Close 421SV518 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV506, 421SV518 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV506, 421SV518

The following table shows the equipment that defines final element leg 1-2 421SV506, 421SV518.

Table 1835 Final Element Leg 1-2: 421SV506, 421SV518 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV506, 421SV518.

Table 1836 Reliability Data Final Element Leg 1-2 421SV506, 421SV518

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: Open 421SV510 (1oo1)

The information and reliability data underneath describe the Open 421SV510 (1oo1) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open 421SV510 (1oo1) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV510 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV510

The following table shows the equipment that defines final element leg 1-1 421SV510.

Table 1837 Final Element Leg 1-1: 421SV510 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV510.

Table 1838 Reliability Data Final Element Leg 1-1 421SV510

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 3.70E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 49.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-323 SIL1 | H2-läckage övre tunnel HH (KD184-911)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2-läckage övre tunnel HH (KD184-911) |
| --- | --- |
| SIF Tag | SIF-323 |
| SIF Description: | Close 421SV501 & Trip 423PU001-STO (2oo2) Close 421SV505 & Close 421SV517 (1oo2) Close 421SV506 & Close 421SV518 (1oo2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 52.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1839 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.89E-02 | 52.9 | 1 | 2 | N/A | 13.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function is quantified as follows.

Table 1840 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.36E-03 | 2 | N/A | 28.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: SIL1 | H2-läckage övre tunnel HH  (KD184-911)

The information and reliability data underneath describe the SIL1 | H2-läckage övre tunnel HH  (KD184-911) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | SIL1 ¦ H2-läckage övre tunnel HH (KD184-911) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | KD184-911 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: KD184-911

The following table shows the equipment that defines sensor leg 1-1 KD184-911.

Table 1841 Sensor Leg 1-1: KD184-911 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Dräger Polytron 8200, 4-20mA sink | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 KD184-911.

Table 1842 Reliability Data Sensor Leg 1-1 KD184-911

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Dräger Polytron 8200, 4-20mA sink | 1.70E-08 - | 1.40E-08 - | 3.26E-06 - | - 3.29E-06 | - - | - - | 2.09E-07 2.09E-07 | - - | 1.40E-08 1.40E-08 | 1.45E-07 1.45E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function is quantified as follows.

Table 1843 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1844 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1845 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911) Safety Instrumented Function is quantified as follows.

Table 1846 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-02 | 2 | N/A | 2206.69 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Close 423SV501 &  Trip 423PU001-STO (2oo2)

The information and reliability data underneath describe the Close 423SV501 &  Trip 423PU001-STO (2oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 423SV501 & Trip 423PU001-STO (2oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423SV501, 423PU001-STO |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 423SV501

The following table shows the equipment that defines final element leg 1 423SV501.

Table 1847 Final Element Leg 1: 423SV501 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 423SV501.

Table 1848 Reliability Data Final Element Leg 1 423SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 423PU001-STO

The following table shows the equipment that defines final element leg 2 423PU001-STO.

Table 1849 Final Element Leg 2: 423PU001-STO Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 423PU001-STO.

Table 1850 Reliability Data Final Element Leg 2 423PU001-STO

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close 421SV505 & Close 421SV517 (1oo2)

The information and reliability data underneath describe the Close 421SV505 & Close 421SV517 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV505 & Close 421SV517 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV505, 421SV517 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV505, 421SV517

The following table shows the equipment that defines final element leg 1-2 421SV505, 421SV517.

Table 1851 Final Element Leg 1-2: 421SV505, 421SV517 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV505, 421SV517.

Table 1852 Reliability Data Final Element Leg 1-2 421SV505, 421SV517

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Close 421SV506  & Close 421SV518 (1oo2)

The information and reliability data underneath describe the Close 421SV506  & Close 421SV518 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV506 & Close 421SV518 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV506, 421SV518 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV506, 421SV518

The following table shows the equipment that defines final element leg 1-2 421SV506, 421SV518.

Table 1853 Final Element Leg 1-2: 421SV506, 421SV518 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV506, 421SV518.

Table 1854 Reliability Data Final Element Leg 1-2 421SV506, 421SV518

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: Open 421SV510 (1oo1)

The information and reliability data underneath describe the Open 421SV510 (1oo1) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open 421SV510 (1oo1) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV510 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV510

The following table shows the equipment that defines final element leg 1-1 421SV510.

Table 1855 Final Element Leg 1-1: 421SV510 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV510.

Table 1856 Reliability Data Final Element Leg 1-1 421SV510

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 3.70E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 49.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913)

This chapter details the SIL Verification results, selections, and assumptions for the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL1 ¦ H2-läckage ventilskåp HH (KD184-913) |
| --- | --- |
| SIF Tag | SIF-324 |
| SIF Description: | Close 421SV501 & Trip 423PU001-STO (2oo2) Close 421SV505 & Close 421SV517 (1oo2) Close 421SV506 & Close 421SV518 (1oo2) |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 1 with RRF ≥ 10 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 1 with RRF = 52.9 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1857 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 1.89E-02 | 52.9 | 1 | 2 | N/A | 13.71 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function is quantified as follows.

Table 1858 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 2.36E-03 | 2 | N/A | 28.14 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: H2-läckage ventilskåp HH (KD184-913)

The information and reliability data underneath describe the H2-läckage ventilskåp HH (KD184-913) sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | H2-läckage ventilskåp HH (KD184-913) |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | KD184-913 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: KD184-913

The following table shows the equipment that defines sensor leg 1-1 KD184-913.

Table 1859 Sensor Leg 1-1: KD184-913 Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Dräger Polytron 8200, 4-20mA sink | 2014.Q2.03 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | 2012.Q1.02 | - | - | B | 2 |
| Analog In Module: AI880A/TU844/845/TY801 | 2012.Q1.02 | - | - | B | 2 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Over Range |
| Out of Range Detection: | On |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | On |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 KD184-913.

Table 1860 Reliability Data Sensor Leg 1-1 KD184-913

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Dräger Polytron 8200, 4-20mA sink | 1.70E-08 - | 1.40E-08 - | 3.26E-06 - | - 3.29E-06 | - - | - - | 2.09E-07 2.09E-07 | - - | 1.40E-08 1.40E-08 | 1.45E-07 1.45E-07 |
| ABB AC800M High Integrity SIL2 [AnalogIn] | - - | - - | - - | 4.28E-09 2.26E-08 | 4.28E-13 4.28E-13 | 1.83E-08 - | 1.83E-12 1.83E-12 | - - | - - | 1.09E-08 1.09E-08 |
| Analog In Module: AI880A/TU844/845/TY801 | - - | - - | - - | 3.69E-07 7.53E-07 | 5.00E-10 5.00E-10 | 3.84E-07 - | 1.32E-10 1.32E-10 | 3.89E-08 3.89E-08 | 3.93E-10 3.93E-10 | 2.11E-07 2.11E-07 |
|  |  |  |  |  |  |  | SFF [%] |  |  | 95.2 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function is quantified as follows.

Table 1861 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1862 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1863 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Analog In Module: AI880A/TU844/845/TY801 | 3.69E-07 | 5.00E-10 | 3.84E-07 | 1.32E-10 | 3.89E-08 | 3.93E-10 | 2.11E-07 |
| Channel: Analog In | 4.28E-09 | 4.28E-13 | 1.83E-08 | 1.83E-12 |  |  | 1.09E-08 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913) Safety Instrumented Function is quantified as follows.

Table 1864 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 1.66E-02 | 2 | N/A | 2206.69 | 0 | 2 |

| Number of Final Element group(s): | 4 |
| --- | --- |
| Voting between groups: | 4oo4 |
| -factor [%]: |  |

#### Final Element Group 1: Close 423SV501 &  Trip 423PU001-STO (2oo2)

The information and reliability data underneath describe the Close 423SV501 &  Trip 423PU001-STO (2oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 423SV501 & Trip 423PU001-STO (2oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 423SV501, 423PU001-STO |
| Voting within group: | 2oo2 |
| Voting type: | Diverse |
| HFT: | 0 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1: 423SV501

The following table shows the equipment that defines final element leg 1 423SV501.

Table 1865 Final Element Leg 1: 423SV501 Details

| Final ELement Leg 1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1 423SV501.

Table 1866 Reliability Data Final Element Leg 1 423SV501

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

##### Final Element Leg 2: 423PU001-STO

The following table shows the equipment that defines final element leg 2 423PU001-STO.

Table 1867 Final Element Leg 2: 423PU001-STO Details

| Final ELement Leg 2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| ASC880 R2 STO |  | - | - | A | 3 |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 2 423PU001-STO.

Table 1868 Reliability Data Final Element Leg 2 423PU001-STO

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| ASC880 R2 STO | - | 1.08E-08 | - | 1.35E-08 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 98.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 2: Close 421SV505 & Close 421SV517 (1oo2)

The information and reliability data underneath describe the Close 421SV505 & Close 421SV517 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV505 & Close 421SV517 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV505, 421SV517 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV505, 421SV517

The following table shows the equipment that defines final element leg 1-2 421SV505, 421SV517.

Table 1869 Final Element Leg 1-2: 421SV505, 421SV517 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV505, 421SV517.

Table 1870 Reliability Data Final Element Leg 1-2 421SV505, 421SV517

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 3: Close 421SV506  & Close 421SV518 (1oo2)

The information and reliability data underneath describe the Close 421SV506  & Close 421SV518 (1oo2) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Close 421SV506 & Close 421SV518 (1oo2) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV506, 421SV518 |
| Voting within group: | 1oo2 |
| Voting type: | Identical |
| HFT: | 1 |
| -factor [%]: | 10 |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-2: 421SV506, 421SV518

The following table shows the equipment that defines final element leg 1-2 421SV506, 421SV518.

Table 1871 Final Element Leg 1-2: 421SV506, 421SV518 Details

| Final ELement Leg 1-2 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-2 421SV506, 421SV518.

Table 1872 Reliability Data Final Element Leg 1-2 421SV506, 421SV518

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 5.55E-07 | - | - | 2.02E-06 |
|  |  |  |  |  | SFF [%] |  | 45.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

#### Final Element Group 4: Open 421SV510 (1oo1)

The information and reliability data underneath describe the Open 421SV510 (1oo1) final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | Open 421SV510 (1oo1) |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV510 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 98 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV510

The following table shows the equipment that defines final element leg 1-1 421SV510.

Table 1873 Final Element Leg 1-1: 421SV510 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Parker N |  | - | - | A | 3 |
| Rotork |  | - | - | A | 3 |
| Pekos Floating Ball Valve, metal seat, < 8" | 2010.1.01 | - | - | A | 3 |

| Valve Open On Trip: | Yes |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV510.

Table 1874 Reliability Data Final Element Leg 1-1 421SV510

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Parker N | - | 5.70E-08 | - | 6.54E-07 | - | - | - |
| Rotork | - | - | - | 3.15E-08 | - | - | - |
| Pekos Floating Ball Valve, metal seat, < 8" | - | - | - | 3.70E-07 | - | - | 2.20E-06 |
|  |  |  |  |  | SFF [%] |  | 49.3 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502

This chapter details the SIL Verification results, selections, and assumptions for the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function.

## General SIF Information

The following characterizes the Safety Instrumented Function.

| SIF Name: | SIL2 ¦ High pressure downstream 421RV503 => close 421SV502 |
| --- | --- |
| SIF Tag | SIF-325 |
| SIF Description: |  |

## Safety Integrity Levels

The target Safety Integrity Level determined for this Safety Instrumented Function is:

|  | SIL 2 with RRF ≥ 100 |
| --- | --- |

The calculated achieved Safety Integrity Level for this Safety Instrumented Function is:

|  | SIL 2 with RRF = 322.8 |
| --- | --- |

## SIL Verification Parameters and Results

This section provides a detailed overview of the Safety Integrity Level verification performed for the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function. In order to perform the reliability calculations part of the Safety Integrity Level verification, the following assumptions have been made.

| Analyst: |  |
| --- | --- |
| Analysis Date: | 02 Dec 2021 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| I/O Channels Allocation: | On separate I/O modules |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 Logic Solver: SSI 2 Final Elements: SSI 2 |
| Include SSI in Failure Rate Selection: | No |
| Comments: |  |

Given the reliability data and SIL verification selections and assumptions described in the subsequent subsections in this report the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function achieves the functional safety performance as displayed in the following table.

Table 1875 SIL Verification Results

| PFDavg | RRF | Achieved SIL |  |  | MTTFS (years) |
| --- | --- | --- | --- | --- | --- |
|  |  | PFDavg | Arch. Constraints IEC 61511 | Systematic Capability |  |
| 3.10E-03 | 322.8 | 2 | 2 | N/A | 16.29 |

The SIF Conceptual Design is modeled as shown in the picture below.

### Sensor Part Configuration

The functional safety and spurious trip behavior of the sensor part of the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function is quantified as follows.

Table 1876 Sensor Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 6.57E-07 | 2 | N/A | 114155.33 | 0 | 2 |

| Number of Sensor group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Sensor Group 1: "Broken Wire"

The information and reliability data underneath describe the "Broken Wire" sensor group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | "Broken Wire" |
| --- | --- |
| Group Description: |  |
| Sensor Legs: | Broken Wire |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: |  |
| Proof Test Execution: | Offline |

##### Sensor Leg 1-1: Broken Wire

The following table shows the equipment that defines sensor leg 1-1 Broken Wire.

Table 1877 Sensor Leg 1-1: Broken Wire Details

| Sensor Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Broken Wire |  | - | - | A | 3 |

| Trip Setting: | High |
| --- | --- |
| Transmitter Fault Direction: | Under Range |
| Out of Range Detection: | Off |
| Transmitter Fault Filter: | Off |
| Trip on Transmitter Fault: | Off |

The Reliability Data table shows the reliability data used during the SIL verification of sensor leg 1-1 Broken Wire.

Table 1878 Reliability Data Sensor Leg 1-1 Broken Wire

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fail Low | Fail High | Fail Det. | SD | SU | DD | DU | AD | AU | NE |
| Broken Wire | - - | - - | - - | - - | 1.00E-09 1.00E-09 | - - | 1.00E-11 1.00E-11 | - - | - - | - - |
|  |  |  |  |  |  |  | SFF [%] |  |  | 99.0 |
|  |  |  |  |  |  |  | Route 2H Compliant |  |  | - |

The data shown in blue and italic indicates the effect of the PLC detection configuration performed by the logic solver on the sensor group data.

The failure rates displayed in red & italic font show the adjusted failure rates due to External Comparison.

### Logic Solver Part Configuration

The functional safety and spurious trip behavior of the logic solver part of the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function is quantified as follows.

Table 1879 Logic Solver Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.11E-06 | 2 | N/A | 27.05 | 0 | 2 |

The information and reliability data underneath describe the ABB AC800M High Integrity SIL2 logic solver group as it has been analyzed in this Safety Integrity Level verification.

| Logic Solver Name: | ABB AC800M High Integrity SIL2 |
| --- | --- |
| Logic Solver Tag: |  |
| Logic Solver Voting: |  |
| HFT: | 0 |
| -factor [%]: |  |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 90 |
| Proof Test Execution: | Offline |

Table 1880 ABB AC800M High Integrity SIL2 Logic Solver Details

| Logic Solver Model | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 | 2012.Q1.02 | - | - | B | N/A |

The Reliability Data table shows the reliability data used during the SIL verification of logic solver group ABB AC800M High Integrity SIL2.

Table 1881 Reliability Data Logic Solver Group ABB AC800M High Integrity SIL2

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 | 4.51E-07 | 7.54E-07 | 1.46E-06 | 1.11E-10 | 3.63E-09 | 1.19E-08 | 6.79E-07 |
| Power Supply: SD823 + SS823 + MCB | 1.53E-06 | 9.06E-10 |  |  | 2.16E-08 | 4.52E-10 | 1.47E-07 |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| Channel: Digital Out | 8.53E-08 | 1.91E-08 |  |  |  |  | 4.07E-08 |
|  |  |  |  |  | SFF [%] |  | 100.0 |

### Final Element Part Configuration

The functional safety and spurious trip behavior of the final element part of the SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502 Safety Instrumented Function is quantified as follows.

Table 1882 Final Element Part SIL Verification Results

| PFDavg | SIL Limits |  | MTTFS (years) | HFT | SSI |
| --- | --- | --- | --- | --- | --- |
|  | Arch. Constraints IEC 61511 | Systematic Capability |  |  |  |
| 3.09E-03 | 2 | N/A | 40.97 | 0 | 2 |

| Number of Final Element group(s): | 1 |
| --- | --- |
| Voting between groups: | 1oo1 |
| -factor [%]: | N/A |

#### Final Element Group 1: close 421SV502

The information and reliability data underneath describe the close 421SV502 final element group as it has been analyzed in this Safety Integrity Level verification.

| Group Name: | close 421SV502 |
| --- | --- |
| Group Description: |  |
| Final Element Legs: | 421SV502 |
| Voting within group: | 1oo1 |
| Voting type: | Identical |
| HFT: | 0 |
| -factor [%]: | N/A |
| MRT [Hours]: | 24 |
| Proof Test Interval [Months]: | 12 |
| Proof Test Coverage [%]: | 64 |
| Proof Test Execution: | Offline |

##### Final Element Leg 1-1: 421SV502

The following table shows the equipment that defines final element leg 1-1 421SV502.

Table 1883 Final Element Leg 1-1: 421SV502 Details

| Final ELement Leg 1-1 | SERH Version | 2H | PIU | AC Type | SIL Cap |
| --- | --- | --- | --- | --- | --- |
| Digital Out Module: DO880/TU842/843 | 2012.Q1.02 | - | - | B | 2 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 2012.Q1.02 | - | - | B | 2 |
| Sages T91 |  | ü | - | A | 2 |

| Valve Open On Trip: | No |
| --- | --- |
| Tight Shutoff Required: | No |
| Severe Service: | No |

The Reliability Data table shows the reliability data used during the SIL verification of final element leg 1-1 421SV502.

Table 1884 Reliability Data Final Element Leg 1-1 421SV502

| Component | Failure Rates [1/hr] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | SD | SU | DD | DU | AD | AU | NE |
| Digital Out Module: DO880/TU842/843 | 3.98E-07 | 9.79E-09 | 4.17E-07 | 1.36E-10 | 3.89E-08 | 3.93E-10 | 3.68E-07 |
| ABB AC800M High Integrity SIL2 [DigitalOut] | 8.53E-08 | 1.91E-08 | - | - | - | - | 4.07E-08 |
| Sages T91 | - | 2.28E-06 | - | 1.14E-07 | - | - | - |
|  |  |  |  |  | SFF [%] |  | 96.6 |
|  |  |  |  |  | Route 2H Compliant |  | - |

The failure rates displayed in blue & italic font show the adjusted failure rates due to the Partial Valve Stroke Test performed.

# SILver™ Group Reuse Overview

This chapter provides an overview of the various groups that were defined during the SIL verification analyses of the Hybrit Pilot Plant project. The reuse of groups is available between Safety Instrumented Functions to account for identical hardware used in those different Safety Instrumented Functions. The group reuse allows users to specify a specific group once, reuse it, and with all future changes made to a single group cascading to all Safety Instrumented Functions it is used in. It is instrumental for the user to review all SIFs a single group is used in when changes are made to that group.

This overview indicates the groups that were reused, the number of times they were reused, and the Safety Instrumented Functions that they were used in.

## Sensor Groups Reused

| Gastryck toppgas (used 4 times) | SIF-013, SIF-014, SIF-011, SIF-012 |
| --- | --- |
| Gastryck transferline (used 3 times) | SIF-021, SIF-024, SIF-020 |
| Tryckvakt O2-inj (used 3 times) | SIF-022, SIF-023, SIF-020 |
| Temperatur konvektionsdel (used 2 times) | SIF-027, SIF-028 |
| High temperature Kanthal 344TI340 -> 345 (used 6 times) | SIF-136, SIF-137, SIF-138, SIF-139, SIF-140, SIF-141 |

## Logic Solver Groups Reused

| ABB AC800M High Integrity SIL3 (used 3 times) | SIF-026, SIF-034, SIF-132 |
| --- | --- |
| ABB AC800M High Integrity SIL2 (used 167 times) | SIF-001, SIF-002, SIF-003, SIF-004, SIF-005, SIF-006, SIF-007, SIF-008, SIF-009, SIF-011, SIF-012, SIF-013, SIF-014, SIF-015, SIF-016, SIF-017, SIF-018, SIF-019, SIF-020, SIF-021, SIF-022, SIF-023, SIF-024, SIF-025, SIF-035, SIF-036, SIF-037, SIF-038, SIF-039, SIF-033, SIF-032, SIF-031, SIF-029, SIF-028, SIF-027, SIF-040, SIF-041, SIF-042, SIF-043, SIF-044, SIF-045, SIF-046, SIF-047, SIF-048, SIF-049, SIF-050, SIF-051, SIF-052, SIF-053, SIF-054, SIF-055, SIF-056, SIF-057, SIF-996, SIF-997, SIF-998, SIF-058, SIF-059, SIF-060, SIF-061, SIF-062, SIF-063, SIF-064, SIF-065, SIF-066, SIF-067, SIF-068, SIF-069, SIF-070, SIF-071, SIF-072, SIF-073, SIF-074, SIF-075, SIF-076, SIF-077, SIF-085, SIF-084, SIF-083, SIF-081, SIF-079, SIF-082, SIF-080, SIF-001, SIF-109, SIF-098, SIF-099, SIF-101, SIF-102, SIF-103, SIF-104, SIF-105, SIF-107, SIF-108, SIF-086, SIF-092, SIF-087, SIF-088, SIF-089, SIF-096, SIF-093, SIF-094, SIF-095, SIF-090, SIF-091, SIF-097, SIF-106, SIF-110, SIF-100, SIF-111, SIF-112, SIF-113, SIF-117, SIF-123, SIF-124, SIF-125, SIF-126, SIF-133, SIF-135, SIF-128, SIF-129, SIF-130, SIF-131, SIF-127, SIF-114, SIF-115, SIF-116, SIF-118, SIF-119, SIF-120, SIF-134, SIF-136, SIF-137, SIF-138, SIF-139, SIF-140, SIF-141, SIF-143, SIF-301, SIF-302, SIF-303, SIF-304, SIF-305, SIF-306, SIF-308, SIF-309, SIF-310, SIF-312, SIF-313, SIF-311, SIF-314, SIF-315, SIF-316, SIF-317, SIF-318, SIF-319, SIF-144, SIF-320, SIF-321, SIF-322, SIF-323, SIF-324, SIF-142, SIF-078, SIF-325, SIF-121, SIF-122 |

## Final Element Groups Reused

| Avstängning O2 (used 4 times) | SIF-037, SIF-043, SIF-044, SIF-079 |
| --- | --- |
| Avstängning-O2 (used 2 times) | SIF-034, SIF-026 |
| Trip red.gaskompressor (used 7 times) | SIF-050, SIF-025, SIF-043, SIF-044, SIF-047, SIF-038, SIF-015 |
| Trip proc.gaskompressor (used 5 times) | SIF-055, SIF-042, SIF-045, SIF-046, SIF-048 |
| Trip red.gaskompressor (used 2 times) | SIF-049, SIF-041 |
| Avstängningsventil 2 överhettad ånga till PGH (used 8 times) | SIF-076, SIF-016, SIF-017, SIF-018, SIF-028, SIF-041, SIF-047, SIF-080 |
| H2 till brännare PGH (used 2 times) | SIF-019, SIF-079 |
| NG till brännare PGH (used 3 times) | SIF-019, SIF-082, SIF-015 |
| O2 inj (used 2 times) | SIF-019, SIF-015 |
| Open Topptryck nödventil eft. spraykylare red. gas (used 2 times) | SIF-013, SIF-123 |
| Close NG till kylkrets (used 4 times) | SIF-042, SIF-045, SIF-046, SIF-048 |
| Avstängning O2 PT12 (used 17 times) | SIF-021, SIF-022, SIF-024, SIF-023, SIF-020, SIF-025, SIF-027, SIF-029, SIF-031, SIF-032, SIF-033, SIF-035, SIF-036, SIF-041, SIF-047, SIF-081, SIF-038 |
| NG till brännare PGH PT12 (used 5 times) | SIF-025, SIF-027, SIF-029, SIF-031, SIF-032 |
| Avstängningsventil 2 överhettad ånga till PGH PT 6 (used 5 times) | SIF-012, SIF-043, SIF-044, SIF-079, SIF-085 |
| Trip Comp. B motor (used 7 times) | SIF-109, SIF-108, SIF-107, SIF-105, SIF-104, SIF-096, SIF-097 |
| Trip Comp. A motor (used 7 times) | SIF-103, SIF-102, SIF-101, SIF-099, SIF-098, SIF-097, SIF-096 |
| PSD A (used 7 times) | SIF-086, SIF-087, SIF-092, SIF-094, SIF-090, SIF-096, SIF-097 |
| Kvävgas till Vätgastank A (open) (used 2 times) | SIF-092, SIF-124 |
| Kvävgas till Vätgastank A (close) (used 2 times) | SIF-092, SIF-124 |
| PSD B (used 8 times) | SIF-088, SIF-089, SIF-093, SIF-095, SIF-091, SIF-096, SIF-097, SIF-125 |
| Close H2 till uppkolningskrets (used 4 times) | SIF-045, SIF-117, SIF-121, SIF-122 |
| Close CO till uppkolningskrets (used 4 times) | SIF-045, SIF-117, SIF-122, SIF-121 |
| Kvävgas till Vätgastank B (open) (used 2 times) | SIF-093, SIF-125 |
| Kvävgas till Vätgastank B (close) (used 2 times) | SIF-093, SIF-125 |
| Close Från Cyklon (used 2 times) | SIF-059, SIF-061 |
| Top gas compressor (354PU101) (used 3 times) | SIF-133, SIF-134, SIF-135 |
| Stop heater 354HE240 (used 3 times) | SIF-114, SIF-115, SIF-116 |
| Stop heater 354HE230 (used 3 times) | SIF-118, SIF-119, SIF-120 |
| vätgaslager kompressor (423PU001) (used 12 times) | SIF-301, SIF-302, SIF-303, SIF-304, SIF-309, SIF-310, SIF-315, SIF-316, SIF-317, SIF-318, SIF-319, SIF-321 |
| 411SV501 & 411SV502 (used 4 times) | SIF-306, SIF-312, SIF-313, SIF-320 |
| 421SV501 & 341SV686 (used 2 times) | SIF-306, SIF-320 |
| close 421SV503 (used 2 times) | SIF-311, SIF-321 |
| close 421SV501 (used 2 times) | SIF-321, SIF-308 |
| Close 423SV501 & Trip 423PU001-STO (2oo2) (used 3 times) | SIF-322, SIF-323, SIF-324 |
| Close 421SV505 & Close 421SV517 (1oo2) (used 3 times) | SIF-322, SIF-323, SIF-324 |
| Close 421SV506 & Close 421SV518 (1oo2) (used 3 times) | SIF-322, SIF-323, SIF-324 |
| Open 421SV510 (1oo1) (used 3 times) | SIF-322, SIF-323, SIF-324 |
| Stop 344HE002 (used 7 times) | SIF-136, SIF-137, SIF-138, SIF-139, SIF-140, SIF-141, SIF-142 |

# Abbreviations and Definitions

## Abbreviations

| HFT | Hardware Fault Tolerance |
| --- | --- |
| IPL | Independent Protection Layers |
| MooN | “M” out of “N” |
| MTTFS | Mean Time To Fail Spurious |
| MRT | Mean Repair Time |
| PFD | Probability of Failure on Demand |
| PFDavg | Average Probability of Failure on Demand |
| PFH | Probability of a Dangerous Failure per Hour |
| PIU | Proven In Use |
| PTC | Proof Test Coverage |
| PTI | Proof Test Interval |
| RRF | Risk Reduction Factor |
| SERH | Safety Equipment Reliability Handbook |
| SFF | Safe Failure Fraction |
| SIF | Safety Instrumented Function |
| SIL | Safety Integrity Level |
| SIS | Safety Instrumented System |
| SSI | Site Safety Index |
| SRS | Safety Requirements Specification |
| -factor | Beta factor, indicating common cause susceptibility |
| SD | Safe Detected |
| SU | Safe Undetected |
| DD | Dangerous Detected |
| DU | Dangerous Undetected |
| AD | Annunciation Detected |
| AU | Annunciation Undetected |
| NE | No Effect |

## Definitions

| Architectural Constraints | Indication of maximum SIL achievable of a SIF’s subsystems architecture based on minimum hardware fault tolerance requirements. This is determined solely on the basis of Type A or Type B device selection, redundancy (hardware fault tolerance), and the safe failure fraction (calculated or conservatively assumed if no data is provided). It does not pertain to Systematic Capability or certification levels. Architectural Constraint limits are determined based on IEC 61508 or IEC 61511 tables. |
| --- | --- |
| Mission Time | This is the time period that the SIF is expected to be operational. Alternatively this is the time period between points in time where the SIF can be considered as new. Note that this is not the proof test interval because of imperfect proof tests considerations. The mission time could, for example, correspond to the major turnaround period of a unit. |
| Startup Time | This represents the time it will take to perform maintenance and repair on a unit after a spurious trip plus the time it will take to restart the unit. This is typically longer than just the average repair time. |
| Systematic Capability | Indication of the maximum SIL achievable based on the SIF’s equipment items systematic integrity alone. This is determined on the basis of the IEC 61508 certification level of each equipment item and/or the systematic integrity claim made by the user for a specific equipment item as part of its Proven In use justification. This addresses the requirement in IEC 61511 that all equipment used in a SIF must either be assessed per IEC 61508 or proven in use. |

# Disclaimer, Assumptions, Equipment Data

## Disclaimer

The user of the exSILentia® software is responsible for verification of all results obtained and their applicability to any particular situation. Calculations are performed per guidelines in applicable international standards. exida Innovation LLC accepts no responsibility for the correctness of the regulations or standards on which the tool is based. In particular, exida Innovation LLC accepts no liability for decisions based on the results of this software. The exida Innovation LLC guarantee is restricted to the correction of errors or deficiencies within a reasonable period when such errors or deficiencies are brought to our attention in writing. exida Innovation LLC accepts no responsibility for adjustments made to this automatically generated report made by the user.

## Assumptions SILver™

SIL Capability

If the user disables the Consider IEC SIL Capability option, it is assumed that the justification of equipment used is performed outside of the SILver tool as in that case the results of the SIL verification only address the quantitative requirements of IEC 61511.

A list of all other assumptions on which the SILver™ tool is based can be found in the exSILentia® user guide.

## Equipment Data

exida has compiled a proprietary equipment failure database. This database is a compilation of failure data collected from a variety of public and confidential sources and presents an industry average. The database is published as the “Safety Equipment Reliability Handbook” ISBN-13: 978-1-934977-15-6. The reliability data collection process as described in this book applies to the SILver equipment data collection process.

The user is responsible for determining the applicability of the failure data to any particular environment. The stress levels assumed to determine the equipment failure rate are average worst case for an industrial environment. Descriptions of the environmental profiles used are included in the Safety Equipment Reliability Handbook. Accurate plant specific data is preferable to general industry average data. Industrial plant sites with high levels of stress must use failure rate data that is adjusted to a higher value to account for the specific conditions of the plant.