# SIL Verification Summary

Hybrit Pilot Plant

| REV | DATE | APPROVED | DESCRIPTION OF CHANGE |
| --- | --- | --- | --- |
|  | 4/24/2022 |  |  |

Automatically generated by ProSa

Table of Contents

1	Purpose and Scope	7

1.1	General Project Information	7

2	SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning	8

3	SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system	10

4	SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100)	12

5	SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100)	14

6	SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101	16

7	SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close	18

8	SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps	20

9	SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608	22

10	SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber	24

11	SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2)	26

12	SIF-011 Beräkning av SIF-011 "open"	28

13	SIF-011 Beräkning av SIF-011 "close"	30

14	SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2)	32

15	SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3)	34

16	SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2)	36

17	SIF-016 SIL1 Temp överhettad ånga (271TI552|L2)	38

18	SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)	40

19	SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)	42

20	SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2)	44

21	SIF-020 SIL2 Difftryck O2-transferline (251XI313)	46

22	SIF-021 SIL1 Gastryck transferline (344PZ321|L2)	48

23	SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2)	50

24	SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2)	52

25	SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)	54

26	SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2)	56

27	SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2)	58

28	SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2)	60

29	SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2)	62

30	SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2)	64

31	SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2)	66

32	SIF-032 SIL2 Flamvakt (344YS314|SG1)	68

33	SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2)	70

34	SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2)	72

35	SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2)	74

36	SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2)	76

37	SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2)	78

38	SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2)	80

39	SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2)	82

40	SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2)	84

41	SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2)	86

42	SIF-042 SIL1 Temp kondensor processgas (353TI301|H2)	88

43	SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2)	90

44	SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2)	92

45	SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2)	94

46	SIF-046 SIL2 Skintemp quench processgas (353TI308|H2)	96

47	SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2)	98

48	SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2)	100

49	SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2)	102

50	SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2)	104

51	SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2)	106

52	SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2)	108

53	SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2)	110

54	SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	112

55	SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2)	114

56	SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	116

57	SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2)	118

58	SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015)	120

59	SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566)	122

60	SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634)	124

61	SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 )	126

62	SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634)	128

63	SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522)	130

64	SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521)	132

65	SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520)	134

66	SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>	136

67	Close Avstängning tillopp spolvatten (345SV634)	137

68	138

69	SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015)	140

70	SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 )	142

71	SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635)	144

72	SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 )	146

73	SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635)	148

74	SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522)	150

75	SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521)	152

76	SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520)	154

77	SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582)	156

78	SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>	158

79	Close Avstängningsventil 2 överhettad ånga till PGH (271SV556)	159

80	SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>	161

81	Close Avstängningsventil O2 efter tankpark (251SV520)	162

82	SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631	164

83	SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2	166

84	SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556	168

85	169

86	SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K	171

87	SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG	173

88	SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)	175

89	SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2)	177

90	SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)	179

91	180

92	SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A	182

93	SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A	184

94	SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B	186

95	SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B	188

96	SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A	190

97	SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B	192

98	SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging	194

99	SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging	196

100	SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A	198

101	SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B	200

102	SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133	202

103	SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133	204

104	SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132	206

105	SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132	208

106	SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926	210

107	SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132	212

108	SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132	214

109	SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133	216

110	SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133	218

111	SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966	220

112	SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133	222

113	SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133	224

114	SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999	226

115	SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132	228

116	SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133	230

117	SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)	232

118	SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start)	233

119	SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240	235

120	SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240	237

121	SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240	239

122	SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2)	241

123	SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230	243

124	SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230	245

125	SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230	247

126	SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2)	249

127	SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2)	251

128	SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3)	253

129	SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging	255

130	SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging	257

131	SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266	259

132	SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar)	261

133	SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326)	263

134	SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326)	265

135	SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5))	267

136	SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5))	269

137	SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2)	271

138	SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100)	273

139	SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2)	275

140	SIF-135 SIL1 High level (347LS305) filter separator 347SE101	277

141	SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002	279

142	SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002	281

143	SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002	283

144	SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002	285

145	SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002	287

146	SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002	289

147	SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater	291

148	SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200	293

149	SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001)	295

150	SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001)	297

151	SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001)	299

152	SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001)	301

153	SIF-305 SIL1|341TI390 HH => Stop 341HE269	303

154	SIF-306 SIL1| Leakage detection 341XI687	305

155	SIF-308 SIL1|421PI305 LL => close 421SV501	307

156	SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001)	309

157	SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001)	311

158	SIF-311 SIL1|  421PI301 > H2 => close 421SV503	313

159	SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB	315

160	SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB	317

161	SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686	319

162	SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001)	321

163	SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001)	323

164	SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001)	325

165	SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001)	327

166	SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001)	329

167	SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900)	331

168	SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901)	333

169	SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910)	335

170	SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911)	337

171	SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913)	339

172	SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502	341

173	Abbreviations and Definitions	343

173.1	Abbreviations	343

174	Disclaimer, Assumptions, Equipment Data	344

174.1	Disclaimer	344

174.2	Assumptions SIL verification (SILver™)	344

# Purpose and Scope

This document, automatically generated by the exida exSILentia® software, summarizes the results of the conceptual design verification for the Safety Instrumented Functions (SIF) for the Hybrit Pilot Plant project.

## General Project Information

| Project Identification: | 001 |
| --- | --- |
| Project Name: | Hybrit Pilot Plant |
| Project Description: |  |

# SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-001 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Low Pressure (254PI330¦L1) nitrogen system, CO2 cleaning |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.46E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 684. MTTFS (years); 16.67. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.37E-03; 208.72; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 8.25E-05; 267.4; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-002 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.69E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 371.9. MTTFS (years); 17.95. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.60E-03; 2044.67; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 8.25E-05; 267.4; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-003 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 High level (347LZ302) in Absorber (347YM100) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.02E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 494. MTTFS (years); 18.81. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.05E-03; 263.52; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 9.68E-04; 1162.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-004 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Low level (347LZ300) in Absorber (347YM100) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.31E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 764.8. MTTFS (years); 18.11. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.20E-03; 272.43; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 9.79E-05; 329.73; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-005 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.29E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 775.8. MTTFS (years); 18.8. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.20E-03; 272.43; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 7.93E-05; 990.65; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-006 SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-006 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Differential pressure treated gas - sour gas (347XI308)-> 347SV672 close and 347SV673 close |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.70E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 369.9. MTTFS (years); 18.18. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.60E-03; 1976.35; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 9.79E-05; 329.73; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-007 SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-007 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 High Temperature (347TI338) after lean MEA cooler close 347SV674 suction side MEA pumps |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 4.21E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 237.2. MTTFS (years); 18.15. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.25E-03; 491.58; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 9.66E-04; 626.52; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-008 SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-008 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 High level (347LZ329 H1) in MEA reboiler (347HE201) close 347RV608 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 2.51E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 39.8. MTTFS (years); 18.79. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.05E-03; 263.52; 2; N/A. Logic Solver Part; 6.90E-06; 20.61; 2; N/A. Final Element Part; 2.40E-02; 1096.4; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-009 SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100)  close 347SV671 lean MEA to Absorber

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-009 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Low differential pressure 347PD339 Pump discharge and absorber (347YM100) close 347SV671 lean MEA to Absorber |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.54E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 650.5. MTTFS (years); 17.04. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.39E-03; 208.73; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.40E-04; 413.74; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-011 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-011 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 2.67E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 373.9. MTTFS (years); 36.73. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 5.04E-05; 3312.46; 3; N/A. Logic Solver Part; 2.76E-06; 37.72; 2; N/A. Final Element Part; 2.62E-03; 2425.2; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-011 Beräkning av SIF-011 "open"

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-011 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | Beräkning av SIF-011 "open" |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 0. PFDavg; 0.00E+00. SIL (PFDavg); 0. SIL (Arch. Constraints IEC 61511); 0. SIL (Systematic Capability); N/A. Achieved RRF; 0. MTTFS (years); ∞. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 0.00E+00; ∞; 0; N/A. Logic Solver Part; 0.00E+00; ∞; -; N/A. Final Element Part; 1.25E-03; 1131.76; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-011 Beräkning av SIF-011 "close"

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-011 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | Beräkning av SIF-011 "close" |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 0. PFDavg; 0.00E+00. SIL (PFDavg); 0. SIL (Arch. Constraints IEC 61511); 0. SIL (Systematic Capability); N/A. Achieved RRF; 0. MTTFS (years); ∞. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 0.00E+00; ∞; 0; N/A. Logic Solver Part; 0.00E+00; ∞; -; N/A. Final Element Part; 3.27E-03; 23908.06; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-012 SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-012 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦L2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 6.74E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 148.3. MTTFS (years); 36.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.31E-05; 3341.86; 3; N/A. Logic Solver Part; 2.46E-06; 37.72; 2; N/A. Final Element Part; 6.69E-03; 2004.76; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-013 Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322|H3)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-013 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | Gastryck toppgas (320PZ320, 320PZ321 & 320PZ322¦H3) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.73E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 57.8. MTTFS (years); 16.73. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.05E-04; 1698.47; 3; N/A. Logic Solver Part; 9.49E-06; 16.94; 2; N/A. Final Element Part; 1.72E-02; 7069.74; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-015 SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-015 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Temp toppgas (320TZ323, 320TZ324 & 320TZ325¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.69E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 175.6. MTTFS (years); 16.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.31E-04; 1693.48; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 5.55E-03; 1170.68; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-016 SIL1 Temp överhettad ånga (271TI552|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-016 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temp överhettad ånga (271TI552¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 9.38E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 106.6. MTTFS (years); 18.29. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.40E-03; 554.98; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-017 SIL1 Tryck överhettad ånga (271PI552|L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-017 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Tryck överhettad ånga (271PI552¦L2) Close Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.77E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 114. MTTFS (years); 17.73. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.86E-04; 284.42; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-018 SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-018 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Tryck överhettad ånga friblåsning (271PI320 < (343PZ305/7/8 + 0,1 barg)) Permissive Avstängningsventil 2 överhettad ånga till PGH (271SV556 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 9.20E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 108.7. MTTFS (years); 18.89. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.22E-03; 13413.9; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-019 SIL2 Flöde reduktionsgas till PGH (343XI302|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-019 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Flöde reduktionsgas till PGH (343XI302¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 4.95E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 201.8. MTTFS (years); 36.56. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.28E-03; 5696.55; 2; N/A. Logic Solver Part; 3.79E-06; 37.91; 2; N/A. Final Element Part; 3.68E-03; 1252.89; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-020 SIL2 Difftryck O2-transferline (251XI313)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-020 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Difftryck O2-transferline (251XI313) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 2.95E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 339. MTTFS (years); 16.24. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 9.06E-04; 1895.34; 2; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-021 SIL1 Gastryck transferline (344PZ321|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-021 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Gastryck transferline (344PZ321¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.83E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 353.6. MTTFS (years); 17.35. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.86E-04; 284.42; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-022 SIL2 Tryckvakt O2-inj (251XI312 |L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-022 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryckvakt O2-inj (251XI312 ¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 2.17E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 461.7. MTTFS (years); 16.24. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.20E-04; 1857.58; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-023 SIL2 Flödesmätare O2 inj (251XI554|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-023 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Flödesmätare O2 inj (251XI554¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 4.24E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 235.6. MTTFS (years); 16.24. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.20E-03; 1971.41; 2; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-024 SIL2 Beräkning difftryck 253XI364|L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-024 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Beräkning difftryck 253XI364¦L1 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 2.94E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 340.7. MTTFS (years); 18.3. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.94E-04; 1886.25; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-025 SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-025 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 4.69E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 213.4. MTTFS (years); 19.08. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.62E-04; 14107.8; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 3.92E-03; 1169.11; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-026 SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-026 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL3 Gastemp transferline (344TZ316, 344TZ317 & 344TZ318¦L2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 3. Target RRF; 1000. Achieved SIL; 3. PFDavg; 8.73E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 3. SIL (Systematic Capability); N/A. Achieved RRF; 1144.8. MTTFS (years); 114.14. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.15E-05; 3591.84; 3; N/A. Logic Solver Part; 9.76E-08; 140.5; 3; N/A. Final Element Part; 8.62E-04; 732.5; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-027 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-027 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 3.92E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 255.3. MTTFS (years); 18.6. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.77E-05; 1878.24; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 3.84E-03; 566.9; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-028 SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-028 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temperatur konvektionsdel (344TZ303, 344TZ304 & 344TZ305¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.06E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); 2. Achieved RRF; 124. MTTFS (years); 18.72. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.77E-05; 1878.24; 3; 3. Logic Solver Part; 7.31E-06; 19.43; 2; 2. Final Element Part; 7.98E-03; 712.98; 2; 3. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-029 SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-029 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temperatur strålningssdel (344TZ310, 344TZ311 & 344TZ312¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 3.92E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 255.3. MTTFS (years); 18.6. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.77E-05; 1878.24; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 3.84E-03; 566.9; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-031 SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-031 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Tryck förbränningskammare (344PZ306, 344PZ307 & 344PZ308¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 3.96E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 252.6. MTTFS (years); 16.46. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.08E-04; 1776.27; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 3.84E-03; 566.9; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-032 SIL2 Flamvakt (344YS314|SG1)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-032 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Flamvakt (344YS314¦SG1) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 4.15E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 241. MTTFS (years); 21.6. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.03E-04; ∞; 2; N/A. Logic Solver Part; 5.24E-06; 22.45; 2; N/A. Final Element Part; 3.84E-03; 566.9; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-033 SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-033 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.17E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 459.7. MTTFS (years); 18.29. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.32E-04; 1775.15; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-034 SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-034 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL3 Gastemp transferline efter O2-inj (344TZ322, 344TZ323 & 344TZ324¦L2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 3. Target RRF; 1000. Achieved SIL; 3. PFDavg; 8.68E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 3. SIL (Systematic Capability); N/A. Achieved RRF; 1151.6. MTTFS (years); 114.14. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.41E-06; 3591.6; 3; N/A. Logic Solver Part; 9.76E-08; 140.5; 3; N/A. Final Element Part; 8.62E-04; 732.5; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-035 SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV|H2/L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-035 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Difftrycksmätning över syreinjektionslans (344XI340_DEV¦H2/L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 6.58E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 151.9. MTTFS (years); 31.96. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 5.53E-03; 745306.04; 2; N/A. Logic Solver Part; 4.87E-06; 33.4; 2; N/A. Final Element Part; 1.06E-03; 738.1; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-036 SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-036 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Gastryck N2 (253PZ362, 253PZ363 & 253PZ364¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.63E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 115.8. MTTFS (years); 18.95. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.17E-04; 10354.69; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 8.21E-03; 842.93; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-037 SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-037 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryckvakt efter N2 bufferttank 253TA005 (253PZ323, 253PZ324, 253PZ325¦L2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.88E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 112.5. MTTFS (years); 36.75. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 5.76E-05; 3622.1; 3; N/A. Logic Solver Part; 2.76E-06; 37.72; 2; N/A. Final Element Part; 8.82E-03; 2390.36; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-038 SIL2 Hög vätskenivå WESP (345LI354/5/6|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-038 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 2.53E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 395.8. MTTFS (years); 17.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.05E-04; 228.67; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 2.12E-03; 1095.15; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-039 SIL2 Tryck efter WESP red. gaskrets (345PI361|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-039 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryck efter WESP red. gaskrets (345PI361¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.32E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 187.9. MTTFS (years); 17.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.89E-04; 273.24; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 4.63E-03; 750.88; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-040 SIL2 Tryck efter WESP processgaskrets (353PI361|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-040 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryck efter WESP processgaskrets (353PI361¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.32E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 187.9. MTTFS (years); 17.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.89E-04; 273.24; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 4.63E-03; 750.88; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-041 SIL1 Temp kondensor reduktionsgas (345TI301|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-041 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temp kondensor reduktionsgas (345TI301¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.15E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 86.6. MTTFS (years); 16.24. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.40E-03; 554.98; 2; N/A. Logic Solver Part; 9.49E-06; 16.94; 2; N/A. Final Element Part; 1.02E-02; 1344.25; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-042 SIL1 Temp kondensor processgas (353TI301|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-042 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Temp kondensor processgas (353TI301¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 5.00E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 199.8. MTTFS (years); 16.23. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.40E-03; 554.98; 2; N/A. Logic Solver Part; 9.49E-06; 16.94; 2; N/A. Final Element Part; 3.60E-03; 1286.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-043 SIL2 Skintemp förquench reduktionsgas (345TI307|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-043 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Skintemp förquench reduktionsgas (345TI307¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.94E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 168.3. MTTFS (years); 28.2. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.20E-04; 1082.88; 2; N/A. Logic Solver Part; 6.05E-06; 29.3; 2; N/A. Final Element Part; 5.22E-03; 2498.19; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-044 SIL2 Skintemp quench reduktionsgas (345TI308|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-044 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Skintemp quench reduktionsgas (345TI308¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.94E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 168.3. MTTFS (years); 28.2. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.20E-04; 1082.88; 2; N/A. Logic Solver Part; 6.05E-06; 29.3; 2; N/A. Final Element Part; 5.22E-03; 2498.19; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-045 SIL2 Skintemp förquench processgas (353TI307|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-045 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Skintemp förquench processgas (353TI307¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 6.49E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 154.1. MTTFS (years); 25.47. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.20E-04; 1082.88; 2; N/A. Logic Solver Part; 7.21E-06; 26.31; 2; N/A. Final Element Part; 5.77E-03; 2975.01; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-046 SIL2 Skintemp quench processgas (353TI308|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-046 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Skintemp quench processgas (353TI308¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.02E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 199. MTTFS (years); 20.6. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.40E-03; 119.15; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 3.63E-03; 314.84; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-047 SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-047 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Flödesmätare till förquench reduktionsgaskrets (345FI305¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.11E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 90.3. MTTFS (years); 12.18. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.01E-03; 33.51; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.01E-02; 1280.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-048 SIL1 Flödesmätare till förquench processgaskrets (353FI305|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-048 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Flödesmätare till förquench processgaskrets (353FI305¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 4.63E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61508); 1. SIL (Systematic Capability); 2. Achieved RRF; 215.7. MTTFS (years); 13.06. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.01E-03; 27.45; 2; 2. Logic Solver Part; 3.11E-06; 27.05; 2; 2. Final Element Part; 3.63E-03; 314.84; 1; 3. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-049 SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300|H2) =>Trip red.gaskompressor (346PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-049 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Hög Nivå kondesseparator inlopp red.gaskompressor (346LI300¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.24E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 445.7. MTTFS (years); 17.74. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.08E-03; 257.02; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-050 SIL2 Gastryck inlopp red.gaskompressor (346PI304|L2) =>Trip red.gaskompressor (346PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-050 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck inlopp red.gaskompressor (346PI304¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.36E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 736.8. MTTFS (years); 17.54. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.27E-03; 220.37; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.93E-05; 990.65; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-051 SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410|H2) =>Trip red.gaskompressor (346PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-051 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastemp eft. kylare red.gaskompressor (oberoende) (346TI410¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.02E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 981.2. MTTFS (years); 17.87. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.59E-04; 287.37; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-052 SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311|H2) =>Trip red.gaskompressor (346PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-052 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Hög Nivå kondensseparator utlopp red.gaskompressor (346LI311¦H2) =>Trip red.gaskompressor (346PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.24E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 445.7. MTTFS (years); 17.74. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.08E-03; 257.02; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-053 SIL2 Lågt oljetryck red.gaskompressor (346PI334|L2) =>Trip red.gaskompressor (346PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-053 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Lågt oljetryck red.gaskompressor (346PI334¦L2) =>Trip red.gaskompressor (346PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.34E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 743.8. MTTFS (years); 17.46. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.18E-03; 208.68; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-054 SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-054 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Hög Nivå kondensseparator inlopp proc.gaskompressor (354LI300¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.24E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 445.7. MTTFS (years); 17.74. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.08E-03; 257.02; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-055 SIL2 Gastryck inlopp proc.gaskompressor (354PI304|L2) =>Trip proc.gaskompressor (354PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-055 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck inlopp proc.gaskompressor (354PI304¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.43E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 699. MTTFS (years); 17.54. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.27E-03; 220.37; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-056 SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-056 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Hög Nivå kondensseparator utlopp proc.gaskompressor (354LI311¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.24E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 445.7. MTTFS (years); 17.74. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.08E-03; 257.02; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-057 SIL2 Lågt oljetryck proc.gaskompressor (354PI354|L2) =>Trip proc.gaskompressor (354PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-057 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Lågt oljetryck proc.gaskompressor (354PI354¦L2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.34E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 743.8. MTTFS (years); 17.46. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.18E-03; 208.68; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-058 SIL1  Syrehalt gasväg (345AZ362|H2) => Trip Högspänningsenhet (345EC015)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-058 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Syrehalt gasväg (345AZ362¦H2) => Trip Högspänningsenhet (345EC015) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.66E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 60.1. MTTFS (years); 14.4. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.30E-02; 151.42; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 3.64E-03; 87.84; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-059 SIL2  Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-059 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätsketryck nedströms pump (345PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(345SV566) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.08E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 123.7. MTTFS (years); 37.14. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.16E-04; 20212.05; 2; N/A. Logic Solver Part; 3.79E-06; 37.91; 2; N/A. Final Element Part; 7.67E-03; 2031.38; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-060 SIL2  Vätskenivå sludge tank (345LS310|H2) => Close Avstängning tillopp spolvatten (345SV634)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-060 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätskenivå sludge tank (345LS310¦H2) => Close Avstängning tillopp spolvatten (345SV634) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.90E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 126.5. MTTFS (years); 18.31. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.69E-04; 576.96; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.23E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-061 SIL2  Vätskenivå sludge tank (345LS312|L2) => Close Avblödning slamvatten (345SV566 )

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-061 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätskenivå sludge tank (345LS312¦L2) => Close Avblödning slamvatten (345SV566 ) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.09E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 123.6. MTTFS (years); 31.67. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.23E-04; 1212.32; 2; N/A. Logic Solver Part; 4.91E-06; 33.05; 2; N/A. Final Element Part; 7.67E-03; 2031.38; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-062 SIL2  Hög vätskenivå WESP (345LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV634)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-062 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Hög vätskenivå WESP (345LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV634) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.64E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 130.9. MTTFS (years); 15.58. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.05E-04; 228.67; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 7.23E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-063 SIL2  Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-063 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (345SV520 & 345SV521) => Open avstängning venturihals(345SV522) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 6.50E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.8. MTTFS (years); 19.53. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 6.29E-03; 372.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-064 SIL2  Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-064 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (345SV520 & 345SV522) => Open avstängning venturihals(345SV521) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.44E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 183.8. MTTFS (years); 20.02. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 5.23E-03; 708.23; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-065 SIL2  Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-065 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (345SV521 & 345SV522) => Open avstängning venturihals(345SV520) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.44E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 183.8. MTTFS (years); 20.02. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 5.23E-03; 708.23; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-066 SIL2  Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) =>

# Close Avstängning tillopp spolvatten (345SV634)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-066 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryckmätare hydrofor ((345PI420/1 )< (320PZ320/1/2 + 0,5 bar)) => Close Avstängning tillopp spolvatten (345SV634) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 3.84E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 260.3. MTTFS (years); 36.51. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 9.18E-05; 3481.2; 3; N/A. Logic Solver Part; 3.79E-06; 37.91; 2; N/A. Final Element Part; 3.75E-03; 1384.78; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-067 SIL1  Syrehalt gasväg (353AZ362|H2) => Trip Högspänningsenhet (353EC015)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-067 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 Syrehalt gasväg (353AZ362¦H2) => Trip Högspänningsenhet (353EC015) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.72E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 58.1. MTTFS (years); 14.4. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.30E-02; 151.42; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 4.22E-03; 87.89; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-068 SIL2  Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 )

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-068 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätsketryck nedströms pump (353PI326 < (320PZ320/1/2 + 0,5 bar)) => Close Avblödning slamvatten(353SV566 ) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.47E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 133.8. MTTFS (years); 18.87. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.65E-04; 10364.55; 2; N/A. Logic Solver Part; 5.42E-06; 19.43; 2; N/A. Final Element Part; 6.71E-03; 709.28; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-069 SIL2  Vätskenivå sludge tank (353LS310|H2) => Close Avstängning tillopp spolvatten (345SV635)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-069 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätskenivå sludge tank (353LS310¦H2) => Close Avstängning tillopp spolvatten (345SV635) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 7.90E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 126.5. MTTFS (years); 18.31. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.69E-04; 576.96; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.23E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-070 SIL2  Vätskenivå sludge tank (353LS312|L2) => Close Avblödning slamvatten (353SV566 )

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-070 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Vätskenivå sludge tank (353LS312¦L2) => Close Avblödning slamvatten (353SV566 ) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 8.05E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 124.2. MTTFS (years); 18.35. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.22E-04; 621.33; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.23E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-071 SIL2  Hög vätskenivå WESP (353LI354/5/6|H2) => Close Avstängning tillopp spolvatten (345SV635)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-071 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Hög vätskenivå WESP (353LI354/5/6¦H2) => Close Avstängning tillopp spolvatten (345SV635) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 7.64E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 130.9. MTTFS (years); 15.58. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.05E-04; 228.67; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 7.23E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-072 SIL2  Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-072 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (353SV520 & 353SV521) => Open avstängning venturihals(353SV522) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 6.50E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.8. MTTFS (years); 19.53. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 6.29E-03; 372.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-073 SIL2  Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-073 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (353SV520 & 353SV522) => Open avstängning venturihals(353SV521) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 5.44E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 183.8. MTTFS (years); 20.02. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 5.23E-03; 708.23; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-074 SIL2  Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-074 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Position avstängning venturihals (353SV521 & 353SV522) => Open avstängning venturihals(353SV520) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 0. Achieved SIL; 2. PFDavg; 5.44E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 183.8. MTTFS (years); 20.02. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.02E-04; 40131.7; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 5.23E-03; 708.23; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-075 SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-075 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryckvakt efter N2 bufferttank 253TA005-reduktionsgastryck ((253PZ323, 253PZ324, 253PZ325) - (343PZ305, 343PZ307, 343PZ308) < 0,5) => Close N2 till reduktionskrets (254SV582) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.36E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 135.8. MTTFS (years); 18.88. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 5.37E-04; 10637.24; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 6.82E-03; 712.14; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-076 SIL2  Hög nivå i ångpanna 271AG001 (271LZ316|H2) =>

# Close Avstängningsventil 2 överhettad ånga till PGH (271SV556)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-076 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Hög nivå i ångpanna 271AG001 (271LZ316¦H2) => Close Avstängningsventil 2 överhettad ånga till PGH (271SV556) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.15E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 122.7. MTTFS (years); 21.61. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.58E-04; 3060.49; 2; N/A. Logic Solver Part; 5.24E-06; 22.45; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-077 Temp efter O2-förångare vid tankparken (251TI300 |L2) =>

# Close Avstängningsventil O2 efter tankpark (251SV520)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-077 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | Temp efter O2-förångare vid tankparken (251TI300 ¦L2) => Close Avstängningsventil O2 efter tankpark (251SV520) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 9.19E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 108.8. MTTFS (years); 18.24. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 513.5; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-078 SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-078 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 253PZ352 (TRYCKMÄTNING 320YM005) => Close 253SV631 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 0. Achieved SIL; 0. PFDavg; 0.00E+00. SIL (PFDavg); 0. SIL (Arch. Constraints IEC 61508); 0. SIL (Systematic Capability); 0. Achieved RRF; 0. MTTFS (years); ∞. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.85E-04; 93.33; 2; 2. Logic Solver Part; 3.11E-06; 27.05; 2; 2. Final Element Part; 0.00E+00; ∞; 0; 0. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-079 SIL2 341PZ401 (H2/L2) =>  close H2

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-079 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 341PZ401 (H2/L2) => close H2 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 6.59E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 151.6. MTTFS (years); 27.36. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.58E-04; 533.14; 2; N/A. Logic Solver Part; 6.05E-06; 29.3; 2; N/A. Final Element Part; 6.24E-03; 1825.59; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-080 SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-080 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 271XI323 Ånga ej tillräckligt överhettad => close 271SV556 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.46E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 68.6. MTTFS (years); 18.9. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.63E-03; 50602.91; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-081 SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-081 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Mätvärde på tillsatt flöde naturgas 252XI565*K |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 3.93E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 254.5. MTTFS (years); 16.33. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.89E-03; 5138.39; 2; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 2.04E-03; 378.21; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-082 SIL2 252PZ337 (H2/L2) =>  close NG

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-082 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 252PZ337 (H2/L2) => close NG |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.78E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 560.9. MTTFS (years); 33.78. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.58E-04; 533.14; 2; N/A. Logic Solver Part; 3.79E-06; 37.91; 2; N/A. Final Element Part; 1.42E-03; 741.34; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-083 Beräkning difftryck 253XI364|L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion)  253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-083 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | Beräkning difftryck 253XI364¦L2 (Skydd mot backflöde processgas till N2 och/eller O2 vid syrgasinjektion) 253XI364 = (2oo3(253PZ362, 253PZ363, 253PZ364) - 344PZ321) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 0. Target RRF; 1. Achieved SIL; 2. PFDavg; 2.71E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 369.2. MTTFS (years); 18.3. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.94E-04; 1886.25; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.81E-03; 377.66; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-084 SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-084 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Hög vätskenivå WESP (353XI354) (353LI354/5/6¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 3.23E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 309.4. MTTFS (years); 17.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.05E-04; 228.67; 3; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 2.82E-03; 1095.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-085 SIL2 Reduktionsgasvärmare trip/ej i drift  (344MA001_RUN_N)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-085 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Reduktionsgasvärmare trip/ej i drift (344MA001_RUN_N) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.98E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 111.3. MTTFS (years); 33.87. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.15E-03; 31371.67; 2; N/A. Logic Solver Part; 3.45E-06; 34.63; 2; N/A. Final Element Part; 4.87E-03; 1638.37; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-086 SIL1 | Lye Temperature H2 A (341TZ300 TZA HH)  => Stop electrolyzer  A

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-086 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Temperature H2 A (341TZ300 TZA HH) => Stop electrolyzer A |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.85E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 145.9. MTTFS (years); 17.7. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-087 SIL1 | Lye Temperature O2 A (341TZ303 TZA HH)  => Stop electrolyzer  A

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-087 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Temperature O2 A (341TZ303 TZA HH) => Stop electrolyzer A |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.85E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 145.9. MTTFS (years); 17.7. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-088 SIL1 | Lye Temperature H2 B (341TZ320 TZA HH)  => Stop electrolyzer B

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-088 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Temperature H2 B (341TZ320 TZA HH) => Stop electrolyzer B |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.85E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 145.9. MTTFS (years); 17.7. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-089 SIL1 | Lye Temperature O2 B (341TZ323 TZA HH)  => Stop electrolyzer  B

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-089 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Temperature O2 B (341TZ323 TZA HH) => Stop electrolyzer B |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.85E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 145.9. MTTFS (years); 17.7. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-090 SIL2 | O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL)  => Stop electrolyzer  A

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-090 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ O2 Separator A Level Transmitter 2 (341LZ306 LZA LLL) => Stop electrolyzer A |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.98E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 167.1. MTTFS (years); 17.48. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.37E-04; 108.08; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-091 SIL2 | O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL)  => Stop electrolyzer  B

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-091 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ O2 Separator B Level Transmitter 2 (341LZ326 LZA LLL) => Stop electrolyzer B |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 5.98E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 167.1. MTTFS (years); 17.48. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.37E-04; 108.08; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-092 SIL1 | O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer  A and successfull nitrogen purging

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-092 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ O2 in H2 A Analyzer (341QZ319 QA HH) => Stop electrolyzer A and successfull nitrogen purging |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 3.22E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 31. MTTFS (years); 24.53. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.90E-03; 306.91; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.74E-02; 1843.7; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-093 SIL1 | O2 in H2 B Analyzer (341QZ339 QA HH)  => Stop electrolyzer B and successfull nitrogen purging

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-093 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ O2 in H2 B Analyzer (341QZ339 QA HH) => Stop electrolyzer B and successfull nitrogen purging |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 3.22E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 31. MTTFS (years); 24.53. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.90E-03; 306.91; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.74E-02; 1843.7; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-094 SIL1 | Lye Flow A (341FZ538 FZA LL)  => Stop electrolyzer  A

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-094 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Flow A (341FZ538 FZA LL) => Stop electrolyzer A |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.57E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 152.2. MTTFS (years); 18.9. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 9.26E-04; 202.31; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-095 SIL1 | Lye Flow B (341FZ578 FZA LL)  => Stop electrolyzer  B

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-095 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lye Flow B (341FZ578 FZA LL) => Stop electrolyzer B |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.57E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 152.3. MTTFS (years); 18.9. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 9.25E-04; 202.31; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-096 SIL1 | H2 Gasholder waterseal (341LZ365 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-096 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2 Gasholder waterseal (341LZ365 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.19E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 83.7. MTTFS (years); 19.78. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.85E-04; 93.33; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.16E-02; 349.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-097 SIL1 | Compressor Waterseal Level (341LZ366 LZA LL)  => Stop electrolyzer  A+B+341PU132+341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-097 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Compressor Waterseal Level (341LZ366 LZA LL) => Stop electrolyzer A+B+341PU132+341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.19E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 83.7. MTTFS (years); 19.78. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.85E-04; 93.33; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.16E-02; 349.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-098 SIL1 | Comp. A Separator 1 level switch H (341LS428 LZA H)  => Stop Comp. A motor 341PU132

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-098 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. A Separator 1 level switch H (341LS428 LZA H) => Stop Comp. A motor 341PU132 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.31E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1203.7. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-099 SIL1 | Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-099 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. A Separator 2 level switch H (341LS438 LZA H) => Stop Comp. A motor 341PU132 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.31E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1203.7. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-100 SIL2 | Comp. A Condensate level switch LL (341LS449 LZA LL )  => Close 341SV926

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-100 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. A Condensate level switch LL (341LS449 LZA LL ) => Close 341SV926 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 112.1. MTTFS (years); 19.95. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.24E-04; 121.88; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.09E-03; 202.2; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-101 SIL1 | Comp. A Outlet pressure transmitter (341PS442 PZA HH)  => Stop Comp. A motor 341PU132

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-101 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. A Outlet pressure transmitter (341PS442 PZA HH) => Stop Comp. A motor 341PU132 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 522.9. MTTFS (years); 20.04. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.75E-03; 119.82; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-102 SIL2 | Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-102 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. A Inlet pressure transmitter (341PS420 PZA LL) => Stop Comp. A motor 341PU132 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 522.9. MTTFS (years); 20.04. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.75E-03; 119.82; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-104 SIL1 | Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-104 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. B Separator 1 level switch H (341LS468 LZA H) => Stop Comp. B motor 341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.31E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1203.7. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-105 SIL1 | Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-105 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. B Separator 2 level switch H (341LS478 LZA H) => Stop Comp. B motor 341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.31E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1203.7. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-106 SIL2 | Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-106 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. B Condensate level switch LL (341LS489 LZA LL) => Close 341SV966 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 112.1. MTTFS (years); 19.95. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.24E-04; 121.88; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.09E-03; 202.2; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-107 SIL1 | Comp. B Outlet pressure transmitter (341PS482 PZA HH)   => Stop Comp. B motor 341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-107 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Comp. B Outlet pressure transmitter (341PS482 PZA HH) => Stop Comp. B motor 341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 522.9. MTTFS (years); 20.04. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.75E-03; 119.82; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-108 SIL2 | Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-108 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. B Inlet pressure transmitter (341PS460 PZA LL) => Stop Comp. B motor 341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 522.9. MTTFS (years); 20.04. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.75E-03; 119.82; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.57E-04; 218.29; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-110 SIL2 | Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-110 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Dryer drain level switch (341LZ499 LZA LL) => Close 341SV999 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.91E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 112.1. MTTFS (years); 19.95. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.24E-04; 121.88; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.09E-03; 202.2; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-111 SIL2 | Comp. A Inlet filter level switch H (341LS423 LZA H)  => Stop Comp. A motor 341PU132

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-111 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. A Inlet filter level switch H (341LS423 LZA H) => Stop Comp. A motor 341PU132 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.65E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1306.5. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 9.14E-05; 218.28; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-112 SIL2 | Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-112 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Comp. B Inlet filter level switch H (341LS463 LZA H ) => Stop Comp. B motor 341PU133 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.65E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1306.5. MTTFS (years); 20.05. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.71E-04; 120.06; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 9.14E-05; 218.28; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-113 SIL2 | Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence)  => Stop electrolyzer  A+B (prevent start)

# SIL2 | Pressure after dryer (341PZ371 L2)  => Stop electrolyzer  A+B (prevent start)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-113 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Pressure after dryer (341PZ371 not H (6 times) during Nitrogen flushing sequence) => Stop electrolyzer A+B (prevent start) SIL2 ¦ Pressure after dryer (341PZ371 L2) => Stop electrolyzer A+B (prevent start) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.50E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 117.5. MTTFS (years); 22.17. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.35E-04; 1254.3; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.27E-03; 136.23; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-114 SIL1 | High temperature Kanthal 354TI442 => stop heater 354HE240

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-114 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 354TI442 => stop heater 354HE240 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.32E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 75.7. MTTFS (years); 16.07. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-115 SIL1 | High temperature Kanthal 354TI443 => stop heater 354HE240

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-115 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 354TI443 => stop heater 354HE240 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.32E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 75.7. MTTFS (years); 16.07. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-116 SIL1 | High temperature Kanthal 354TI444 => stop heater 354HE240

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-116 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 354TI444 => stop heater 354HE240 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.32E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 75.7. MTTFS (years); 16.07. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-117 SIL1 | Temp kondensor processgas (321XI319|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-117 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Temp kondensor processgas (321XI319¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.13E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 88.4. MTTFS (years); 24.25. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.32E-04; 585.39; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.12E-02; 391.09; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-118 SIL1 | High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-118 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Chromalox 354TI331 and 354TI332 (1oo2) => stop heater 354HE230 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.27E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 78.6. MTTFS (years); 13.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.86E-04; 56.31; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-119 SIL1 | High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-119 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Chromalox 354TI335 and 354TI336 (1oo2) => stop heater 354HE230 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.27E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 78.6. MTTFS (years); 13.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.86E-04; 56.31; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-120 SIL1 | High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-120 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Chromalox 354TI339 and 354TI340 (1oo2) => stop heater 354HE230 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.27E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 78.6. MTTFS (years); 13.62. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.86E-04; 56.31; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.23E-02; 53.46; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-121 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-121 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦H2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 7.56E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 132.1. MTTFS (years); 23.94. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.17E-05; 2036.08; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 7.50E-03; 231.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-122 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|L2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-122 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦L2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 7.64E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 130.9. MTTFS (years); 24.01. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.17E-05; 2036.08; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 7.57E-03; 238.57; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-123 SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317|H3)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-123 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastryck nedre krets (321PI315, 321PI316 & 321PI317¦H3) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 8.89E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 112.5. MTTFS (years); 51.4. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.20E-05; 3972.77; 3; N/A. Logic Solver Part; 1.62E-06; 52.78; 2; N/A. Final Element Part; 8.85E-03; 3915.32; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-124 SIL1 | Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-124 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Low flow to O2 in H2 A Analyzer (341FS315 FZA LL) => Stop electrolyzer A and successfull nitrogen purging |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 2.86E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 34.9. MTTFS (years); 23.76. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.18E-03; 219.04; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.74E-02; 1843.7; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-125 SIL1 | Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-125 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Low flow to O2 in H2 B Analyzer (341FS335 FZA LL) => Stop electrolyzer B and successfull nitrogen purging |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 2.86E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 34.9. MTTFS (years); 23.76. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.18E-03; 219.04; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.74E-02; 1843.7; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-126 SIL1 | Dryer heater outlet temperature transmitter (341TI341 TZA HH)  => Stop heater 341HE266

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-126 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Dryer heater outlet temperature transmitter (341TI341 TZA HH) => Stop heater 341HE266 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 4.48E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 223.4. MTTFS (years); 19.45. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.30E-04; 292.22; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 4.14E-03; 90.82; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-127 SIL2  Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-127 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Tryckmätare hydrofor (345PI420/1 )< (321PI315/6/7 + 1,0 bar) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.41E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 134.9. MTTFS (years); 16.56. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.77E-04; 1785.73; 3; N/A. Logic Solver Part; 9.40E-06; 17.12; 2; N/A. Final Element Part; 7.22E-03; 709.66; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-128 SIL1 | Difftryck, H2 – Processgas 354XI327|L2 (341PI882 - 354PI326)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-128 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Difftryck, H2 – Processgas 354XI327¦L2 (341PI882 - 354PI326) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.48E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 67.5. MTTFS (years); 18.91. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.03E-03; 268851.38; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 6.82E-03; 712.14; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-129 SIL1 | Difftryck, CO – Processgas 354XI328|L2 (356PI311 - 354PI326)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-129 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Difftryck, CO – Processgas 354XI328¦L2 (356PI311 - 354PI326) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.14E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 88. MTTFS (years); 18.89. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.40E-03; 19570.98; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 7.98E-03; 712.98; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-130 SIL1 | Difftryck H2-linje till red.krets 343XI308|L2 (341PI675<(343PZ305/7/8+0,5))

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-130 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Difftryck H2-linje till red.krets 343XI308¦L2 (341PI675<(343PZ305/7/8+0,5)) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 9.79E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 102.1. MTTFS (years); 18.89. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.98E-03; 13531.06; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 6.82E-03; 712.14; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-131 SIL1 | Difftryck NG-linje till red.krets 343XI307|L2 (252PI565<(343PZ305/7/8+0,5))

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-131 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Difftryck NG-linje till red.krets 343XI307¦L2 (252PI565<(343PZ305/7/8+0,5)) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 5.09E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 196.5. MTTFS (years); 36.85. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.56E-03; 26399.15; 2; N/A. Logic Solver Part; 3.79E-06; 37.91; 2; N/A. Final Element Part; 3.54E-03; 1389.63; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-132 SIL3 | High pressure downstream of 356RV558  => close 356SV563 & 356SV564 (1oo2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-132 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL3 ¦ High pressure downstream of 356RV558 => close 356SV563 & 356SV564 (1oo2) |
| Mission Time |  | 10 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 3. Target RRF; 1000. Achieved SIL; 3. PFDavg; 8.87E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 3. SIL (Systematic Capability); N/A. Achieved RRF; 1127.6. MTTFS (years); 48.9. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.40E-05; 151.73; 3; N/A. Logic Solver Part; 2.25E-08; 144; 3; N/A. Final Element Part; 8.53E-04; 144.66; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-133 SIL1 High level (347LZ302) in Absorber (347YM100)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-133 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 High level (347LZ302) in Absorber (347YM100) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 2.02E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 494. MTTFS (years); 18.81. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.05E-03; 263.52; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 9.68E-04; 1162.95; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-134 SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410|H2) =>Trip proc.gaskompressor (354PU101 SIL2)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-134 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 Gastemp eft. kylare proc.gaskompressor (oberoende) (354TI410¦H2) =>Trip proc.gaskompressor (354PU101 SIL2) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 1.56E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 642.4. MTTFS (years); 18.42. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.40E-03; 554.98; 2; N/A. Logic Solver Part; 7.31E-06; 19.43; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-135 SIL1 High level (347LS305) filter separator 347SE101

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-135 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 High level (347LS305) filter separator 347SE101 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.36E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 734.1. MTTFS (years); 18.8. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.20E-03; 272.43; 2; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 1.53E-04; 990.72; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-136 SIL1 | High temperature Kanthal 344TI340 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-136 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI340 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-137 SIL1 | High temperature Kanthal 344TI341 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-137 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI341 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-138 SIL1 | High temperature Kanthal 344TI342 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-138 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI342 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-139 SIL1 | High temperature Kanthal 344TI343 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-139 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI343 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-140 SIL1 | High temperature Kanthal 344TI344 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-140 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI344 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-141 SIL1 | High temperature Kanthal 344TI345 => stop heater 344HE002

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-141 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ High temperature Kanthal 344TI345 => stop heater 344HE002 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 6.51E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 153.5. MTTFS (years); 18.34. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 8.72E-04; 152.59; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-143 SIL1 | 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-143 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ 343HV500_Ej GSO och / eller 343HV501_Ej GSS => Trip fired heater |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 7.11E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 140.7. MTTFS (years); 19.81. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.34E-06; 2409.2; 3; N/A. Logic Solver Part; 6.90E-06; 20.62; 2; N/A. Final Element Part; 7.09E-03; 642.01; 3; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-144 SIL1| High tempertature in (356TI308) => trip 356HE200

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-144 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦ High tempertature in (356TI308) => trip 356HE200 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 4.76E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 210.1. MTTFS (years); 17.68. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.15E-04; 116.43; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 4.14E-03; 90.82; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-301 SIL1|Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-301 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦Temperature stage 1 (423TI301) HH => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.38E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 724.9. MTTFS (years); 19.96. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-302 SIL1|Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-302 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦Temperature stage 2 (423TI302) HH => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.38E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 724.9. MTTFS (years); 19.96. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-303 SIL1|Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-303 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦Temperature stage 3 (423TI303) HH => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.38E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 724.9. MTTFS (years); 19.96. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.21E-03; 117.1; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-304 SIL1|High Pressure compressor (423PI304) HH => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-304 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦High Pressure compressor (423PI304) HH => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 5.54E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1806.2. MTTFS (years); 19.13. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 3.85E-04; 93.33; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-305 SIL1|341TI390 HH => Stop 341HE269

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-305 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦341TI390 HH => Stop 341HE269 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 8.15E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 122.6. MTTFS (years); 18.91. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.52E-03; 203; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 5.64E-03; 90.96; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-306 SIL1| Leakage detection 341XI687

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-306 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦ Leakage detection 341XI687 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 1. PFDavg; 3.30E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 30.3. MTTFS (years); 26.21. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.22E-03; 1179.31; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.89E-02; 3025.17; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-308 SIL1|421PI305 LL => close 421SV501

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-308 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦421PI305 LL => close 421SV501 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 8.47E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 118.1. MTTFS (years); 19.09. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.71E-04; 95.6; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.00E-03; 202.18; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-309 SIL2| 423PI301 LL => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-309 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2¦ 423PI301 LL => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 3.04E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 3287.3. MTTFS (years); 23.49. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.36E-04; 988.53; 3; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-310 SIL2|421TI304 HH  => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-310 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2¦421TI304 HH => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 1.58E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 633.8. MTTFS (years); 21.54. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 1.41E-03; 205.17; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-311 SIL1|  421PI301 > H2 => close 421SV503

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-311 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1¦ 421PI301 > H2 => close 421SV503 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 8.78E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 113.8. MTTFS (years); 20.66. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 7.89E-04; 154.33; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 8.00E-03; 202.18; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-312 SIL2 | Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-312 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Tryck i koksgasledning SSAB (411PI302) L2 => Block & bleed to SSAB |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 1. PFDavg; 1.56E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 64.2. MTTFS (years); 20.86. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.71E-04; 95.6; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.51E-02; 2017.84; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-313 SIL2 | Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-313 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ Tryck i koksgasledning SSAB (411PI302) H2 => Block & bleed to SSAB |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 1. PFDavg; 1.56E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 64.2. MTTFS (years); 20.86. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.71E-04; 95.6; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.51E-02; 2017.84; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-314 SIL1 | Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-314 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Tryck L2 i pipeline P1 <-> P3 (341PI687) => close 341SV686 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; TBD. Target RRF; 1. Achieved SIL; 2. PFDavg; 7.30E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 136.9. MTTFS (years); 19.09. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 4.71E-04; 95.6; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 6.83E-03; 201.94; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-315 SIL1 | Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-315 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Motortemperatur lindning 1 (423PU001-TI1) => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 7.83E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1276.4. MTTFS (years); 19.94. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.15E-04; 116.43; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-316 SIL1 | Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-316 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Motortemperatur lindning 2 (423PU001-TI2) => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 7.83E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1276.4. MTTFS (years); 19.94. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.15E-04; 116.43; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-317 SIL1 | Motortemperatur lindning 3 (423PU001-TI3) =>  Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-317 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Motortemperatur lindning 3 (423PU001-TI3) => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 7.83E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1276.4. MTTFS (years); 19.94. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.15E-04; 116.43; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-318 SIL1 | Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-318 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lagertemperatur (423PU001-TI11) => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 1.13E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 883.8. MTTFS (years); 20.09. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 9.63E-04; 121.68; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-319 SIL1 | Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-319 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ Lagertemperatur (423PU001-TI12) => Stop Compressor (423PU001) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 2. PFDavg; 7.83E-04. SIL (PFDavg); 3. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 1276.4. MTTFS (years); 19.94. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.15E-04; 116.43; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-04; 218.3; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-320 SIL1 |  H2-läckage i kulvert (LKAB) HH (KD184-900)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-320 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2-läckage i kulvert (LKAB) HH (KD184-900) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 3.12E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 32. MTTFS (years); 13.73. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.36E-03; 28.14; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 2.89E-02; 3025.17; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-321 SIL1 | H2-läckage i kompressorstation HH (KD184-901)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-321 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2-läckage i kompressorstation HH (KD184-901) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.84E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 54.3. MTTFS (years); 13.31. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.36E-03; 28.14; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.61E-02; 380.73; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-322 SIL1 | H2-läckage i tunnelmynning (tunnelport) HH (KD184-910)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-322 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2-läckage i tunnelmynning (tunnelport) HH (KD184-910) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.89E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 52.9. MTTFS (years); 13.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.36E-03; 28.14; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-02; 2206.69; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-323 SIL1 | H2-läckage övre tunnel HH  (KD184-911)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-323 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2-läckage övre tunnel HH (KD184-911) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.89E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 52.9. MTTFS (years); 13.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.36E-03; 28.14; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-02; 2206.69; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-324 SIL1 | H2-läckage ventilskåp HH (KD184-913)

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-324 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL1 ¦ H2-läckage ventilskåp HH (KD184-913) |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 1. Target RRF; 10. Achieved SIL; 1. PFDavg; 1.89E-02. SIL (PFDavg); 1. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 52.9. MTTFS (years); 13.71. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 2.36E-03; 28.14; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 1.66E-02; 2206.69; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# SIF-325 SIL2 | High pressure downstream 421RV503 => close 421SV502

| Project Name |  | Hybrit Pilot Plant | SIF Tag | SIF-325 |
| --- | --- | --- | --- | --- |
| Unit / Process Area |  |  | SIF Name | SIL2 ¦ High pressure downstream 421RV503 => close 421SV502 |
| Mission Time |  | 15 years |  |  |
| Safety Instrumented Function Performance. Target SIL; 2. Target RRF; 100. Achieved SIL; 2. PFDavg; 3.10E-03. SIL (PFDavg); 2. SIL (Arch. Constraints IEC 61511); 2. SIL (Systematic Capability); N/A. Achieved RRF; 322.8. MTTFS (years); 16.29. | PFDavg; MTTFS; SIL Limit. AC; CAP. Sensor Part; 6.57E-07; 114155.33; 2; N/A. Logic Solver Part; 3.11E-06; 27.05; 2; N/A. Final Element Part; 3.09E-03; 40.97; 2; N/A. |
| Remarks | The SIF operates in Low demand mode. |  |  |  |
| Note: The results shown in this SIL verification Summary are based on detailed calculations. All SIL verification assumptions including used reliability data are documented in the SIL verification Details report. |  |  |  |  |

# Abbreviations and Definitions

## Abbreviations

| MTTFS | Mean Time To Fail Spurious |
| --- | --- |
| MTTR | Mean Time To Restore |
| PFD | Probability of Failure on Demand |
| PFDAVG | Average Probability of Failure on Demand |
| PFH | Probability of a Dangerous Failure per Hour |
| PTI | Proof Test Interval |
| RRF | Risk Reduction Factor |
| SIF | Safety Instrumented Function |
| SIL | Safety Integrity Level |
| SIS | Safety Instrumented System |

# Disclaimer, Assumptions, Equipment Data

## Disclaimer

The user of the exSILentia® software is responsible for verification of all results obtained and their applicability to any particular situation. Calculations are performed per guidelines in applicable international standards. exida.com L.L.C. accepts no responsibility for the correctness of the regulations or standards on which the tool is based. In particular, exida.com L.L.C. accepts no liability for decisions based on the results of this software. The exida.com L.L.C. guarantee is restricted to the correction of errors or deficiencies within a reasonable period when such errors or deficiencies are brought to its attention in writing. exida.com L.L.C. accepts no responsibility for adjustments made by the user to this automatically generated report.

## Assumptions SIL verification (SILver™)

A detailed list of assumptions upon which the exSILentia®’s SILver™ SIL verifications are based are documented in the user guide. The user guide is available as PDF as well as embedded within the exSILentia® software Help menu. The user is assumed to be knowledgeable with regard to the parameter selections and the, potential, impact on the operation of the respective Safety Instrumented Functions and Safety Instrumented System.

Conceptual design selection details are included in the SIL verification Details report.