SIL Verification Report

Project

| Project ID: | 1 |
| --- | --- |
| Customer: | — |
| Revision: | A |
| Date: | 2026-05-30 |

Automatically generated by SIL Verification Tool (Excel)

Table of Contents

No table of contents entries found.

Purpose and Scope

This document summarizes the results of the conceptual design verification for the Safety Instrumented Functions (SIF) in the Project. The verification is performed in accordance with IEC 61511 / IEC 61508 using simplified equations for low demand mode of operation.

General Project Information

| Project Identification: | 1 |
| --- | --- |
| Project Name: | Project |
| Customer: | — |
| Project Description: | — |
| Analyst: | — |
| Reviewer: | — |
| Approver: | — |
| Revision: | A |
| Date: | 2026-05-30 |

Document Control

| REV | DATE | APPROVED | DESCRIPTION OF CHANGE |
| --- | --- | --- | --- |
| A | 2026-05-30 |  | Initial issue |

SIF-001 SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 4,00E+00 | 236 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 97,5 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-002 SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 6,00E+00 | 160 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 97,5 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-003 SIL1 High level (347LZ302) in Absorber (347YM100)

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,00E+00 | 777 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 92,2 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 90 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-004 SIL2 Low level (347LZ300) in Absorber (347YM100)

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 2 with RRF ≥ 100

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 6,00E+00 | 150 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 6,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-005 SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,00E+00 | 810 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 99 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-006 New SIF — edit description

General SIF Information

| Analyst: |  |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: |  |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: |  |

Safety Integrity Levels

Target SIL: SIL 2 with RRF ≥ 100

SIL Verification Parameters and Results

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,00E+00 | 810 | 2 | YES |

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 99 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

Disclaimer, Assumptions, Equipment Data

Disclaimer

The results shown in this SIL verification Report are based on the design data, failure rates and proof test parameters provided. Accuracy of the result is dependent on the accuracy of the input data.

Assumptions

Low demand mode of operation per IEC 61511-1.

Simplified PFD equations per IEC 61508-6, Annex B.

Constant failure rate (exponential distribution).

Common cause modeled via β-factor (Beta model).

Single-leg / single-group per subsystem (sum of component λ-values).

Architectural constraints (Route 1H/2H, SFF, HFT) not automatically verified.

Verification Status

This tool has been validated against the Hybrit Pilot Plant SILver Detailed Report (24 Apr 2022, exSILentia v4.12.2). For SIF-001 through SIF-005, the achieved SIL classification matches in 5 of 5 cases. The geometric mean PFD ratio (Tool / Report) is 1.84×.