SIL Verification Report

Project

| Project ID: | 1 |
| --- | --- |
| Customer: | — |
| Revision: | A |
| Date: | 2026-05-30 |

Automatically generated by SIL Verification Tool (Excel)

Table of Contents

No table of contents entries found.

Purpose and Scope

This document summarizes the results of the conceptual design verification for the Safety Instrumented Functions (SIF) in the Project. The verification is performed in accordance with IEC 61511 / IEC 61508 using simplified equations for low demand mode of operation.

General Project Information

| Project Identification: | 1 |
| --- | --- |
| Project Name: | Project |
| Customer: | — |
| Project Description: | — |
| Analyst: | — |
| Reviewer: | — |
| Approver: | — |
| Revision: | A |
| Date: | 2026-05-30 |

Document Control

| REV | DATE | APPROVED | DESCRIPTION OF CHANGE |
| --- | --- | --- | --- |
| A | 2026-05-30 | — | Initial issue |

SIF-001 — SIL1 Low Pressure (254PI330|L1) nitrogen system, CO2 cleaning

SIF Overview

Target SIL: SIL 1    |    Achieved SIL: 2    |    PFDavg: 4,23E-03    |    RRF: 236

Sensor (1oo1)

• Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75

• PR Electronics 9106, 1 active in/1 active out

• ABB AC800M High Integrity SIL2 [AnalogIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Analog In Module: AI880A/TU844/845/TY801

• Channel: Analog In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo2)

• ABB AC800M High Integrity SIL2 [DigitalOut]

• Metso Norgren

• Metso VPVL

• Metso 7000 9000

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 4,23E-03 | 236 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 97,5 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-002 — SIL1 Low differential pressure (254PI330 / 347PI306) Nitrogen system

SIF Overview

Target SIL: SIL 1    |    Achieved SIL: 2    |    PFDavg: 6,24E-03    |    RRF: 160

Sensor (2oo2)

• Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75

• PR Electronics 9106, 1 active in/1 active out

• ABB AC800M High Integrity SIL2 [AnalogIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Analog In Module: AI880A/TU844/845/TY801

• Channel: Analog In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo2)

• ABB AC800M High Integrity SIL2 [DigitalOut]

• Metso Norgren

• Metso VPVL

• Metso 7000 9000

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 6,24E-03 | 160 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Cerabar S PMP71, PMP72 HT, PMP75 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 97,5 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-003 — SIL1 High level (347LZ302) in Absorber (347YM100)

SIF Overview

Target SIL: SIL 1    |    Achieved SIL: 2    |    PFDavg: 1,29E-03    |    RRF: 777

Sensor (1oo1)

• Endress+Hauser Liquiphant M/S + FEL 58

• PR Electronics 9202, relay output

• ABB AC800M High Integrity SIL2 [DigitalIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Digital In Module: DI880/TU842/843

• Channel: Digitial In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo1)

• ASC880 R2 STO

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,29E-03 | 777 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 92,2 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 90 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-004 — SIL2 Low level (347LZ300) in Absorber (347YM100)

SIF Overview

Target SIL: SIL 2    |    Achieved SIL: 2    |    PFDavg: 6,66E-03    |    RRF: 150

Sensor (1oo1)

• Endress+Hauser Deltabar S PMD75, FMD77, FMD78

• PR Electronics 9106, 1 active in/1 active out

• ABB AC800M High Integrity SIL2 [AnalogIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Analog In Module: AI880A/TU844/845/TY801

• Channel: Analog In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo2)

• ABB AC800M High Integrity SIL2 [DigitalOut]

• Metso Norgren

• Metso VPVL

• Metso 7000 9000

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 2 with RRF ≥ 100

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 6,66E-03 | 150 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Deltabar S PMD75, FMD77, FMD78 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9106, 1 active in/1 active out |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [AnalogIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 6,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Analog In Module: AI880A/TU844/845/TY801 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Analog In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ABB AC800M High Integrity SIL2 [DigitalOut] |  |  |  | 0,00E+00 |  |  |  |
| Metso Norgren |  |  |  | 0,00E+00 |  |  |  |
| Metso VPVL |  |  |  | 0,00E+00 |  |  |  |
| Metso 7000 9000 |  |  |  | 0,00E+00 |  |  |  |
| β-factor [%]: |  |  |  | 10 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 2,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-005 — SIL1 High level (347LS305) filter separator 347SE101 stop 346PU101

SIF Overview

Target SIL: SIL 1    |    Achieved SIL: 2    |    PFDavg: 1,23E-03    |    RRF: 810

Sensor (1oo1)

• Endress+Hauser Liquiphant M/S + FEL 58

• PR Electronics 9202, relay output

• ABB AC800M High Integrity SIL2 [DigitalIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Digital In Module: DI880/TU842/843

• Channel: Digitial In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo1)

• ASC880 R2 STO

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 1 with RRF ≥ 10

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,23E-03 | 810 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 99 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

SIF-006 — New SIF — edit description

SIF Overview

Target SIL: SIL 2    |    Achieved SIL: 2    |    PFDavg: 1,23E-03    |    RRF: 810

Sensor (1oo1)

• Endress+Hauser Liquiphant M/S + FEL 58

• PR Electronics 9202, relay output

• ABB AC800M High Integrity SIL2 [DigitalIn]

↓ Logic Solver (1oo1)

• Main Processor: PM865/PM867 with SM810/SM811/SM812

• Power Supply: SD823 + SS823 + MCB

• Digital In Module: DI880/TU842/843

• Channel: Digitial In

• Digital Out Module: DO880/TU842/843

• Channel: Digital Out

↓ Final Element (1oo1)

• ASC880 R2 STO

General SIF Information

| Analyst: | — |
| --- | --- |
| Analysis Date: | 30 May 2026 |
| Design References: | — |
| Mission Time: | 15 years |
| Startup Time: | 24 hours |
| Demand Mode: | Low |
| Architectural Constraints: | IEC 61511 |
| Consider Systematic Capability: | No |
| Consider MTTFS: | Yes |
| Site Safety Index: | Sensors: SSI 2 ¦ LS: SSI 2 ¦ FE: SSI 2 |
| Comments: | — |

Safety Integrity Levels

Target SIL: SIL 2 with RRF ≥ 100

Verification Result

| PFDavg | RRF | Achieved SIL | Target met |
| --- | --- | --- | --- |
| 1,23E-03 | 810 | 2 | YES |

Subsystem Configurations

Sensor Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Endress+Hauser Liquiphant M/S + FEL 58 |  |  |  | 0,00E+00 |  |  |  |
| PR Electronics 9202, relay output |  |  |  | 0,00E+00 |  |  |  |
| ABB AC800M High Integrity SIL2 [DigitalIn] |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 91,9 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 1,00E+00 |  |  |  |

Logic Solver Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Main Processor: PM865/PM867 with SM810/SM811/SM812 |  |  |  | 0,00E+00 |  |  |  |
| Power Supply: SD823 + SS823 + MCB |  |  |  | 0,00E+00 |  |  |  |
| Digital In Module: DI880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digitial In |  |  |  | 0,00E+00 |  |  |  |
| Digital Out Module: DO880/TU842/843 |  |  |  | 0,00E+00 |  |  |  |
| Channel: Digital Out |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Final Element Part Configuration

| Component |  |  |  | λNE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASC880 R2 STO |  |  |  | 0,00E+00 |  |  |  |
| Proof Test Interval [Months]: |  |  |  | 12 |  |  |  |
| MRT [Hours]: |  |  |  | 24 |  |  |  |
| Proof Test Coverage [%]: |  |  |  | 99 |  |  |  |
| β-factor [%]: |  |  |  | 0 |  |  |  |
| ΣλDU [1/h]: |  |  |  | 0,00E+00 |  |  |  |
| PFDavg: |  |  |  | 0,00E+00 |  |  |  |

Diagrams

PFD Contribution per Subsystem

MTTFS Contribution per Subsystem

PFD vs Time (sawtooth)

Disclaimer, Assumptions, Equipment Data

Disclaimer

The results shown in this SIL verification Report are based on the design data, failure rates and proof test parameters provided.

Assumptions

Low demand mode of operation per IEC 61511-1.

Simplified PFD equations per IEC 61508-6, Annex B.

Constant failure rate (exponential distribution).

Common cause modeled via β-factor (Beta model).