SIL Verification Summary

[Customer] — [Project / Plant]

Project ID: 1

Revision A · 2026-05-30

Automatically generated from SIL Verification Tool (Excel/VBA)

Document Control

| # REV | # DATE | # APPROVED | # DESCRIPTION OF CHANGE |
| --- | --- | --- | --- |
| # A | # 2026-05-30 |  | # Initial issue |

Purpose and Scope

This document summarizes the results of the conceptual design verification for the Safety Instrumented Functions (SIF) in the [Project / Plant] for [Customer]. The verification is performed in accordance with IEC 61511 / IEC 61508 using simplified equations for low demand mode of operation.

General Project Information

| ## Customer | ## [Customer] |
| --- | --- |
| ## Project Name | ## [Project / Plant] |
| ## Project Identification | ## 1 |
| ## Project Description |  |
| ## Designer |  |
| ## Reviewer |  |
| ## Approver |  |
| ## Date | ## 2026-05-30 |

SIF-001 SIL2

| # Project Name | # [Project / Plant] | # SIF Tag | # SIF-001 |
| --- | --- | --- | --- |
| # Customer | # [Customer] | # SIF Name |  |
| # Unit / Process Area |  | # Target SIL | # 2 |
| # Mission Time | # 15 years | # Demand Mode | # Low |
| # Remarks | # The SIF operates in Low demand mode. |  |  |
| # Standard | # IEC 61511 / IEC 61508 | # Method | # Simplified equations |

SIF Architecture and Subsystem Inputs

| ## Parameter | ## Sensor | ## Logic Solver | ## Final Element |
| --- | --- | --- | --- |
| ## Architecture | ## 2oo2 | ## 1oo1 | ## 1oo1 |
| ## ?DU (FIT) | ## 57 | ## 18 | ## 26 |
| ## ?DD (FIT) | ## 17 | ## 17 | ## 57 |
| ## Proof Test Interval (h) | ## 8 760 | ## 8 760 | ## 8 760 |
| ## MTTR (h) | ## 8 | ## 8 | ## 24 |
| ## Mission Time (h) | ## 87 600 | ## 87 600 | ## 87 600 |
| ## PTC | ## 90,0% | ## 90,0% | ## 90,0% |
| ## ß / ßD | ## 10,0% / 5,0% | ## 5,0% / 2,5% | ## 10,0% / 5,0% |

Verification Result

| ## Item | ## Value | ## Contribution |
| --- | --- | --- |
| ## PFDavg Sensor | ## 5,00E-04 | ## 57,6% |
| ## PFDavg Logic Solver | ## 1,50E-04 | ## 17,3% |
| ## PFDavg Final Element | ## 2,18E-04 | ## 25,1% |
| ## Total PFDavg | ## 8,67E-04 | ## 100.0% |
| ## Achieved SIL | ## 3 |  |
| ## Risk Reduction Factor | ## 1 153 |  |

Target SIL: 2    |    Achieved SIL: 3    |    Target met: YES

Disclaimer, Assumptions, Equipment Data

Disclaimer

The results shown in this SIL verification Summary are based on the design data, failure rates and proof test parameters provided. Accuracy of the result is dependent on the accuracy of the input data.

Assumptions

• Low demand mode of operation per IEC 61511-1.

• Simplified PFD equations per IEC 61508-6, Annex B.

• Constant failure rate (exponential distribution).

• Common cause modeled via ß-factor (Beta model).